## Instructions
INSTRUCTIONS: |  | Sizing Conduit / Tubing - Instructions and Information | [9 empty] | This spreadsheet was developed by WireLab Services, and is provided at no cost (you get what you pay for). The NEC superceeds any and all information found herein.
Enter your data into the sizing Conduit worksheet in the following order:
|  |  |  | This is a caution or warning window which pops us whenever a condition may exist which could jeopardize the calculations or raceway size. |  |  | This cell displays the minimum size available raceway which the NEC will allow for the selected conductors and/or cables. Whenever it is not selected (indicated by wihite arrow), it is still somewhat visible. |  | This white arror points to the selected raceway size that is being used for raceway calculations by the bottom section of this screen
Step 1 - Select the type raceway for the job using the pull down box.
Step 2 - Select whether or not the raceway will be a nipple using the pulldown box. (one of the pull down boxes is shown here.)
If any errors are found, however, please contact the following so that they can be corrected and redistributed:
Step 3 - Enter the conductors and/or cables for Group Rows 1 - 10 as follows:.
- Enter the quantity of the first group of conductors and/orcables on Group Row 1.
| - If you are installing conductors in raceways, select the type of conductor and the wire size using the pull down boxes on Group Row 1. | [10 empty] | Bill_Bamford @ Yahoo.com
- If you are installing cables in raceways, enter the diameter of the cable using either decimals or fractions on Group Row 1.
These two cells are only visible when all conductors or cables are of the same type and size.
If you have more than one size conductor or cable, enter their data on the next Group row, repeating step three for up to ten groups of conductors/cables in the raceway.
Step 4 - If you want to override the NEC minimum size raceway, select Yes in the pull down box. | [11 empty] | This window is only visible when there is a possibility of jamming per Table 1 Inform-ational Note 2. If only 3 conductors or cables are in the conduit and they are of the same type and size, the jamming ratio is calculated
Step 5 - If you selected to overide the NEC minimum size raceway, you must select a raceway size using the pull down box.
The total number of all wire and/or cable types or sizes
The total number of all wires and/or cables
This cell contain the NEC fill % allowance
This cell contains the actual fill %. Occassionally, this % will exceed the allowable fill allowance because the NEC does not count 20% of one wire or cable if all wires and cables in the raceway are the same size per note 7.
[8 empty] | When only 3 wires or cables are entered, this cell displays the jamming ratio for the selected raceway per Informational Note 2 |  | Chapter 9 Tables
The total sq" of all conductors and cables.
Table 1 gives the percent fill allowance for all types of raceways.
This Instruction Worksheet |  |  |  |  | The total available sq" inside the selected raceway.
Sizing Conduit/Tubing Worksheet | [7 empty] | This cell displays the inside diameter of the selected raceway. |  |  | Informational Note:1 States that the percent fill allowed by table one will not necessarily be adequate for all conditions.
WireLab Brochure Worksheet |  |  |  | The total fill % as calculated by note 7 of chapter 9.
INFORMATION: | [7 empty] | This cell displays the inside diameter of the selected conductor.
The total area of all conductors minus 20% of one wire as calculated by note 7 of Chapter 9.
Informational Note:2 States that jamming can occur when pulling three conductors/cables into a raceway if the jamming ratio is between 2.8 and 3.2.
Chapter 9 All the codes and tables used for sizing conduit and tubing (round raceways) are taken from chapter 9. There are 5 tables with two informational notes on Table 1, and nine notes to the chapter 9 tables which provide the requirements for sizing round raceways: | [6 empty] | Chapter 9 Notes to Tables
|  |  | Note 1 allows the use of NEC Annex C (an informational note) for making raceway calculations when all conductors are the same size in the raceway. |  |  |  | Note 5 states that conductors not included in Chapter nine, such as multiconductor cables, must be manually calculated using their actual dimensions. This spreadsheet allows the input of cables by inputing their widest diameter using either decimal or fractions. |  | Note 8 states that bare conductors which are allowed in conduit/tubing must be sized by Table 8.
Table 4 provides the diameters and % fill area of most types of conduit and tubing allowed by the NEC.
Note 2 allows larger fill for conduit/tubing that will only be used to protect exposed wiring from physical damage. It can be filled to 100%.
Note: If either a 3/8" FMC, or LFMC is indicated, check NEC Table 348.22 before installing the conduit to verify the installation. The NEC does not give tubing sizes for FNT other than for 3/8" in Table 348.22 and therefore is not supported with this spreadsheet. | [6 empty] | Note 6 states that if a combination of conductors of different sizes or types are used, then Tables 5 and 5A and Table 4 provide the sq" required for calculations. |  | Note 9 states that multiconductor cables shall be treated as a single conductor for calculating the fill% by measuring the diameter of cables at their widest point. | Table 5 provides the diameters and the square inches for most insulated conductors and fixture wires allowed by the NEC.
|  |  | Note 3 states that equipment grounding or bonding conductors must also be included when calculating the total conductor area. |  |  |  | Note 7 states that if all conductors in the raceway are the same size, then the total area of all conductors can be reduced by 20% of one conductor. Note 7 is used by Annex C when it ocassionaly allows an extra wire in the raceway such as: 22 each 14AWG THHN wires in 3/4" instead of 1" EMT. This spreadsheet accomplishes this by adding the square inches of all of the wires or cables and then subtracting 20% of one of the wires or cables to give the square" to be used.
Table 5A provides the diameters and the square inches for all compact aluminum conductors allowed by the NEC, including bare compact aluminum conductors.
Annex C - If all of the conductors are the same size, Annex C has raceway tables with calculations based on Chapter 9 reqiirements. Just find the raceway type and look up the conductor size to determine the raceway size. The Annex C tables are not used for cables, mixed conductor sizes, bare wires, or for nipples. |  |  | Note 4 states that nipples 24" in length or shorter can be filled to 60%. When sizing the wires inside of nipples, the adjustment factors of Table 310.15(B)(3)(a) need not be applied. This spreadsheet only allows 31% fill for 2 conductors in nipples.
Table 8 provides the diameters and the square inches for bare copper and aluminum conductors.

## Sizing Conduit
This Excel Spreadsheet was developed by WireLab Services which specializes in resources for electricians. It is provided for use at no cost and may be freely copied and shared as long as it is not modified in any way.
Sizing Conduit / Tubing | [10 empty] | CAUTION: CHECK JAMMING RATION BELOW! Chapter 9, Table 1, Informational Note 2 of the NEC warns that "JAMMING" can occur whenever 3 equal sized conductors or cables are run in conduit or tubing and the ratio between the inside diameter of the conduit or tubing divided by one of the wire's or cables diameter is between 2.8 and 3.2. | [13 empty] | This Excel Spreadsheet was developed by WireLab Services which specializes in resources for electricians. It is provided for use at no cost and may be freely copied and shared as long as it is not modified in any way.
Per 2011 NEC
| Complete in order the following 4-5 steps: | [9 empty] | The white arrow below indicates the selected raceway size:
|  | 1. Select type of Conduit or Tubing: |  |  |  |  | EMT (Thinwall) | [12 empty] | NEC's Minimum Size Raceway = | 1" | <
|  | 2. Use this pull down box to Indicate whether this is for a nipple: | [8 empty] | No | 4. Use this pull down box to override the NEC raceway size : | [8 empty] | No
No
|  | 3. Enter all conductors and/or cables below using pull down boxes: | [9 empty] | 5. Use this pull down box to select an override raceway size: | [63 empty] | Mike Holt provides two other Wirelab Services products on his excellent Website "MikeHolt.com". One is a handout on conduit bending and the other is a spreadsheet on voltage drop calculations.
Mike Holt provides two other WireLab Services products on his excellent Website "MikeHolt.com". One is a handout on conduit bending and the other is a spreadsheet on voltage drop calculations.
|  | Group | Qty | Single conductors | [5 empty] | Wire Size |  | Dia. | Area | Total Area |  |  | Qty | Cable Dia. |  | Area | Total Area
|  | 1 | 3 | THHN, THWN, THWN-2 | [5 empty] | 2 |  | 0.384 | 0.1158 | 0.3474 | sq" |  | 3 |  |  | 0 | 0 | sq"
|  | 2 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq"
|  | 3 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq"
|  | 4 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq"
|  | 5 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq"
|  | 6 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq"
|  | 7 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq" | [53 empty] | While every effort has been made to achieve a work of high quality, the author does not guarantee the accuracy of this spreadsheet. Please report any errors found, so that they can be corrected and redistributed. Send to: Bill_Bamford@Yahoo.com
|  | 8 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq" |  |  | While every effort has been made to achieve a work of high quality, the author does not guarantee the accuracy of this spreadsheet. Please report any errors found, so that they can be corrected and redistributed. Send to: Bill_Bamford@Yahoo.com
|  | 9 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq"
|  | 10 | [9 empty] | 0 | 0 |  | sq" |  |  |  |  | 0 | 0 | sq"
Cable diameters can be decimal or fraction.
Number of wire/cable sizes = | [5 empty] | 1 | 100% of all wires/cables = |  |  |  |  | 0.3474 |  | sq" |  | OK - Jamming Ratio = |  |  |  |  | 2.7318
Number of conductors/cables = | [5 empty] | 3 |  |  |  |  | Total inside area of raceway = | 0.864 |  | sq" |  | Inside Diameter of raceway = |  |  |  |  | 1.049 | "
Selected Fill Percentage = | [5 empty] | 40% | 100% - (20% of 1 wire) = |  |  |  |  | 37.53% |  |  |  | Diameter of one conductor = |  |  |  |  | 0.384 | "
[5 empty] | Actual raceway fill % = | 40.21% |  | 100% - (20% of 1 wire) = |  |  |  | 0.32424 |  | sq" |  | Last updated - April 4, 2012
*Ch9 Table 1 Note 7 is tabulated into these figures, which should give the same results as Annex C
Only Enter Data into Yellow Cells | [6 empty] | Calculated information | [5 empty] | Bad Results | [5 empty] | Good Results
Warning: Do not use cut and paste on the yellow cells. It messes up the pull down lists. If you do, you may have to reload the entire program.
[7 empty] | Group | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  | Yes |  | 1" | = Selected raceway size
1 |  |  | Insulation Types |  |  |  | WS | 1: 9 |  | No |  | ok | = This overide size of raceway is too small
2 |  | 1 | THHN, THWN, THWN-2 |  |  |  | 9 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.32424 |  | 0.4 | = selected percentage
3 |  | 2 | THW, THW-2, THHW, TW |  |  |  | 8 | 12 | [13 empty] | Error Message = : | 2 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
4 |  | 3 | XHH, XHHW, XHHW-2 |  |  |  | 8 | 10 | [9 empty] | 1 | WARNING! The conduit selected does not have a size large enough for the conductors or cables. |  |  |  | 3 | 0 |  | 18 | 18 | 8 | 6 | 14 | 14 | 14 | 14 | 14 | 18 | 18 | 18 | 18 | 16
5 |  | 4 | THHN [Compact Alum.] |  |  |  | 4 | 8 | [14 empty] | 1 | 0 |  | 16 | 16 | 6 | 4 | 12 | 12 | 12 | 12 | 12 | 16 | 16 | 16
6 |  | 5 | THHW, THW [Compact Alum.] |  |  |  | 3 | 6 | [14 empty] | 4 | 0 |  | 14 | 14 | 4 | 2 | 10 | 10 | 10 | 10 | 10 |  | 14 | 14
7 |  | 6 | XHHW [Compact Alum.] |  |  |  | 3 | 4 | [14 empty] | 5 | 0 |  | 12 | 12 | 2 | 1 | 8 | 8 | 8 | 8 | 8 |  | 12
8 |  | 7 | FEP, FEPB |  |  |  | 5 | 3 | [9 empty] | 2 | CAUTION: CHECK JAMMING RATION BELOW! Chapter 9, Table 1, Informational Note 2 of the NEC warns that "JAMMING" can occur whenever 3 equal sized conductors or cables are run in conduit or tubing and the ratio between the inside diameter of the conduit or tubing divided by one of the wire's or cables diameter is between 2.8 and 3.2. |  |  |  | 6 | 0 |  | 10 | 10 | 1 | 1/0 | 6 | 6 | 6 | 6 | 6 |  | 10
9 |  | 8 | PFA |  |  |  | 6 | 2 | [14 empty] | 7 | 0 |  | 8 | 8 | 1/0 | 2/0 | 4 | 4 | 4 | 4 | 4
10 |  | 9 | PFAH, TFE |  |  |  | 7 | 1 | [14 empty] | 2 | 2 |  | 2: 6; 3: 2/0; 4: 3/0; 5: 3; 6: 3; 7: 3; 8: 3; 9: 3
11 |  | 10 | RHH*, RHW*, RHW-2* without covering |  |  |  | 8 | 1/0 | [17 empty] | 2: 4; 3: 3/0; 4: 4/0; 5: 2; 6: 2; 7: 2; 8: 2; 9: 2
12 |  | 11 | RHH, RHW, RHW-2 with covering |  |  |  | 8 | 2/0 | [17 empty] | 2: 3; 3: 4/0; 4: 250; 6: 1/0; 7: 1; 8: 1; 9: 1
13 |  | 12 | BARE - Solid |  |  |  | 1 | 3/0 | [9 empty] | 3 | NO CONDUIT OR TUBING HAS BEEN SELECTED! Complete Steps 1-3 Select a conduit or tubing from the pull down box on Line 1! | [6 empty] | 2: 2; 3: 250; 4: 300; 6: 2/0; 7: 1/0; 8: 1/0; 9: 1/0
14 |  | 13 | BARE - Stranded |  |  |  | 2 | 4/0 | [17 empty] | 2: 1; 3: 300; 4: 350; 6: 3/0; 7: 2/0; 8: 2/0; 9: 2/0
15 |  | 14 | BARE - [Compact Alum.] |  |  |  | 3 | 250 | [17 empty] | 2: 1/0; 3: 350; 4: 400; 6: 4/0; 7: 3/0; 8: 3/0; 9: 3/0
16 |  | 15 | Z |  |  |  | 7 | 300 | [17 empty] | 2: 2/0; 3: 400; 4: 500; 7: 4/0; 8: 4/0; 9: 4/0
17 |  | 16 | ZW |  |  |  | 5 | 350 | [17 empty] | 2: 3/0; 3: 500; 4: 600; 8: 250; 9: 250
18 |  | 17 | FFH-2, RFH-2 |  |  |  | 10 | 400 | [9 empty] | 4 | ERROR! The wire size selected is not available for the selected insulation, select a new wire size from the pull down list! | [6 empty] | 2: 4/0; 3: 600; 4: 700; 8: 300; 9: 300
19 |  | 18 | KF-1, KFF-1 |  |  |  | 11 | 500 | [17 empty] | 2: 250; 3: 700; 4: 750; 8: 350; 9: 350
20 |  | 19 | KF-2, KFF-2 |  |  |  | 11 | 600 | [17 empty] | 2: 300; 3: 750; 4: 900; 8: 400; 9: 400
21 |  | 20 | PAF, PAFF, PF, PFF |  |  |  | 12 | 700 | [17 empty] | 2: 350; 3: 900; 4: 1000; 8: 500; 9: 500
22 |  | 21 | PGF, PGFF, PTF, PTFF |  |  |  | 12 | 750 | [17 empty] | 2: 400; 3: 1000; 8: 600; 9: 600
23 |  | 22 | RFH-1 |  |  |  | 13 | 800 | [9 empty] | 5 | CAUTION! You must only use the first row when you have 3 equal size conductors! | [6 empty] | 2: 500; 8: 700; 9: 700
24 |  | 23 | SF-1, SFF-1 |  |  |  | 13 | 900 | [17 empty] | 2: 600; 8: 750; 9: 750
25 |  | 24 | SF-2, SFF-2 |  |  |  | 12 | 1000 | [17 empty] | 2: 700; 8: 800; 9: 800
26 |  | 25 | TF, TFF |  |  |  | 14 | [18 empty] | 2: 750; 8: 900; 9: 900
27 |  | 26 | TFN, TFFN |  |  |  | 10 | [18 empty] | 2: 800; 8: 1000; 9: 1000
28 |  | 27 | XF, XFF |  |  |  | 11 | [10 empty] | 6 | CAUTION! You must only use the first row when you have 3 equal size conductors! | [6 empty] | 2: 900; 8: 1250
|  | 28 | ZF, ZFF |  |  |  | 12 | [18 empty] | 2: 1000; 8: 1500
|  |  | Warning: Don't move the cells in this column around because the cells in AK33-60 will also change. | [22 empty] | 2: 1250; 8: 1750
[27 empty] | 1500 | [5 empty] | 2000
1750
[18 empty] | 7 | Caution! Check with NEC Table 348.22 before using the selected 3/8" raceway! | [6 empty] | 2: 2000
Min
|  | sq" | Selected conduit:
|  | 0.32424 |  |  | Fill | 40% | 60% | 31% | 53%
|  | 1 | EMT (Thinwall) |  |  | 1" | 1" | 1 1/4" | 1"
|  | 2 | ENT (Smurf pipe) |  |  | 1 1/4" | 1" | 1 1/4" | 1"
|  | 3 | FMC (Greenfield) |  |  | 1" | 1" | 1 1/4" | 1"
|  | 4 | IMC |  |  | 1" | 3/4" | 1 1/4" | 1"
|  | 5 | LFNC-B (Carlon) |  |  | 1" | 3/4" | 1 1/4" | 1"
|  | 6 | LFNC-A (Orange) |  |  | 1" | 1" | 1 1/4" | 1"
|  | 7 | LFMC (Sealtite) |  |  | 1" | 3/4" | 1 1/4" | 1"
|  | 8 | RMC (Rigid) |  |  | 1" | 3/4" | 1 1/4" | 1"
|  | 9 | PVC (Schedule 80) |  |  | 1 1/4" | 1" | 1 1/4" | 1"
|  | 10 | PVC (Schedule 40) |  |  | 1" | 1" | 1 1/4" | 1"
|  | 11 | PVC (Type A) |  |  | 1" | 3/4" | 1" | 3/4"
|  | 12 | PVC (Type EB) |  |  | 3" | 3" | 3" | 3"
|  |  | Sizing Conduit and Tubing Charts | [40 empty] | Sizing Conduit and Tubing Charts
|  |  | Three or More Conductors (40% Fill) | [21 empty] | Two Conductors (31% Fill) | [18 empty] | Three or More Conductors (40% Fill) | [16 empty] | Two Conductors (31% Fill)
|  |  | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | [6 empty] | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" |  |  |  | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" |  | Conduit Sizes: | 3/8 " | 1/2" | 3/4" | 1" | 1 1/4 | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6"
|  |  | EMT (Thinwall) |  |  |  | 0.122 | 0.213 | 0.346 | 0.598 | 0.814 | 1.342 | 2.343 | 3.538 | 4.618 | 5.901 |  |  | 1" | [5 empty] | EMT (Thinwall) |  |  |  | 0.094 | 0.165 | 0.268 | 0.464 | 0.631 | 1.04 | 1.816 | 2.742 | 3.579 | 4.573 |  |  | 1 1/4" |  |  | EMT (Thinwall) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15 | EMT (Thinwall) |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 13
|  |  | ENT (Smurf pipe) |  |  |  | 0.099 | 0.181 | 0.314 | 0.564 | 0.774 | 1.282 | [6 empty] | 1 1/4" | [5 empty] | ENT (Smurf pipe) | 4: 0.076; 5: 0.141; 6: 0.243; 7: 0.437; 8: 0.6; 9: 0.993 |  | 1 1/4" |  |  | ENT (Smurf pipe) |  |  |  | 0 | 0 | 0 | 1 | 2 | 2 | [6 empty] | 5 | ENT (Smurf pipe) |  | 0 | 0 | 0 | 1 | 2 | 2 | [6 empty] | 5
|  |  | FMC (Greenfield) |  |  | 0.046 | 0.127 | 0.213 | 0.327 | 0.511 | 0.743 | 1.307 | 1.963 | 2.827 | 3.848 | 5.027 |  |  | 1" | [5 empty] | FMC (Greenfield) |  |  | 0.036 | 0.098 | 0.165 | 0.253 | 0.396 | 0.576 | 1.013 | 1.522 | 2.191 | 2.983 | 3.896 |  |  | 1 1/4" |  |  | FMC (Greenfield) |  |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15 | FMC (Greenfield) | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 13
|  |  | IMC |  |  |  | 0.137 | 0.235 | 0.384 | 0.659 | 0.89 | 1.452 | 2.054 | 3.169 | 4.234 | 5.452 |  |  | 1" | [5 empty] | IMC |  |  |  | 0.106 | 0.182 | 0.297 | 0.51 | 0.69 | 1.125 | 1.592 | 2.456 | 3.281 | 4.226 |  |  | 1 1/4" |  |  | IMC |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15 | IMC |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 13
|  |  | LFNC-B (Carlon) |  |  | 0.077 | 0.125 | 0.216 | 0.349 | 0.611 | 0.792 | 1.298 | [6 empty] | 1" | [5 empty] | LFNC-B (Carlon) | 3: 0.059; 4: 0.097; 5: 0.168; 6: 0.27; 7: 0.474; 8: 0.614; 9: 1.006 |  | 1 1/4" |  |  | LFNC-B (Carlon) |  |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | [6 empty] | 7 | LFNC-B (Carlon) | 0 | 0 | 0 | 0 | 1 | 2 | 2 | [6 empty] | 5
|  |  | LFNC-A (Orange) |  |  | 0.077 | 0.125 | 0.214 | 0.342 | 0.601 | 0.807 | 1.337 | [6 empty] | 1" | [5 empty] | LFNC-A (Orange) | 3: 0.06; 4: 0.097; 5: 0.166; 6: 0.265; 7: 0.466; 8: 0.626; 9: 1.036 |  | 1 1/4" |  |  | LFNC-A (Orange) |  |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | [6 empty] | 7 | LFNC-A (Orange) | 0 | 0 | 0 | 0 | 1 | 2 | 2 | [6 empty] | 5
|  |  | LFMC (Sealtite) |  |  | 0.077 | 0.125 | 0.216 | 0.349 | 0.611 | 0.792 | 1.298 | 1.953 | 2.99 | 3.893 | 5.077 |  |  | 1" | [5 empty] | LFMC (Sealtite) |  |  | 0.059 | 0.097 | 0.168 | 0.27 | 0.474 | 0.614 | 1.006 | 1.513 | 2.317 | 3.017 | 3.935 |  |  | 1 1/4" |  |  | LFMC (Sealtite) |  |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15 | LFMC (Sealtite) | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 13
|  |  | RMC (Rigid) |  |  |  | 0.125 | 0.22 | 0.355 | 0.61 | 0.829 | 1.363 | 1.946 | 3 | 4.004 | 5.153 | 8.085 | 11.663 | 1" | [5 empty] | RMC (Rigid) |  |  |  | 0.097 | 0.17 | 0.275 | 0.473 | 0.642 | 1.056 | 1.508 | 2.325 | 3.103 | 3.994 | 6.266 | 9.039 | 1 1/4" |  |  | RMC (Rigid) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19 | RMC (Rigid) |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 17
|  |  | PVC (Schedule 80) |  |  |  | 0.087 | 0.164 | 0.275 | 0.495 | 0.684 | 1.15 | 1.647 | 2.577 | 3.475 | 4.503 | 7.142 | 10.239 | 1 1/4" | [5 empty] | PVC (Schedule 80) |  |  |  | 0.067 | 0.127 | 0.213 | 0.383 | 0.53 | 0.891 | 1.277 | 1.997 | 2.693 | 3.49 | 5.535 | 7.935 | 1 1/4" |  |  | PVC (Schedule 80) |  |  |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 17 | PVC (Schedule 80) |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 17
|  |  | PVC (Schedule 40) |  |  |  | 0.114 | 0.203 | 0.333 | 0.581 | 0.794 | 1.316 | 1.878 | 2.907 | 3.895 | 5.022 | 7.904 | 11.427 | 1" | [5 empty] | PVC (Schedule 40) |  |  |  | 0.088 | 0.157 | 0.258 | 0.45 | 0.616 | 1.02 | 1.455 | 2.253 | 3.018 | 3.892 | 6.126 | 8.856 | 1 1/4" |  |  | PVC (Schedule 40) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19 | PVC (Schedule 40) |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 17
|  |  | PVC (Type A) |  |  |  | 0.154 | 0.26 | 0.434 | 0.707 | 0.929 | 1.459 | 2.181 | 3.278 | 4.278 | 5.489 |  |  | 1" | [5 empty] | PVC (Type A) |  |  |  | 0.119 | 0.202 | 0.336 | 0.548 | 0.72 | 1.131 | 1.69 | 2.54 | 3.315 | 4.254 |  |  | 1" |  |  | PVC (Type A) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15 | PVC (Type A) |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15
|  |  | PVC (Type EB) | [8 empty] | 1.55 |  | 3.484 | 4.546 | 5.779 | 8.878 | 12.612 | 3" | [5 empty] | PVC (Type EB) | 9: 1.201; 11: 2.7; 12: 3.523; 13: 4.479; 14: 6.881 | 9.774 | 3" |  |  | PVC (Type EB) | [8 empty] | 1 |  | 1 | 2 | 2 | 2 | 2 | 10 | PVC (Type EB) | [6 empty] | 1 |  | 1 | 2 | 2 | 2 | 2 | 10
|  |  | Nipple (60% Fill) | [21 empty] | One Conductor (53% Fill) | [18 empty] | Nipple (60% Fill) | [16 empty] | One Conductor (53% Fill)
|  |  | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | [6 empty] | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" |  |  |  | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" |  | Conduit Sizes: | 3/8 " | 1/2" | 3/4" | 1" | 1 1/4 | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6"
|  |  | EMT (Thinwall) |  |  |  | 0.182 | 0.32 | 0.519 | 0.897 | 1.221 | 2.013 | 3.515 | 5.307 | 6.927 | 8.852 |  |  | 1" | [5 empty] | EMT (Thinwall) |  |  |  | 0.161 | 0.283 | 0.458 | 0.793 | 1.079 | 1.778 | 3.105 | 4.688 | 6.119 | 7.819 |  |  | 1" |  |  | EMT (Thinwall) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15 | EMT (Thinwall) |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15
|  |  | ENT (Smurf pipe) |  |  |  | 0.148 | 0.272 | 0.471 | 0.846 | 1.162 | 1.923 | [6 empty] | 1" | [5 empty] | ENT (Smurf pipe) | 4: 0.131; 5: 0.24; 6: 0.416; 7: 0.747; 8: 1.026; 9: 1.699 |  | 1" |  |  | ENT (Smurf pipe) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | [6 empty] | 7 | ENT (Smurf pipe) |  | 0 | 0 | 1 | 2 | 2 | 2 | [6 empty] | 7
|  |  | FMC (Greenfield) |  |  | 0.069 | 0.19 | 0.32 | 0.49 | 0.766 | 1.115 | 1.961 | 2.945 | 4.241 | 5.773 | 7.54 |  |  | 1" | [5 empty] | FMC (Greenfield) |  |  | 0.061 | 0.168 | 0.283 | 0.433 | 0.677 | 0.985 | 1.732 | 2.602 | 3.746 | 5.099 | 6.66 |  |  | 1" |  |  | FMC (Greenfield) |  |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15 | FMC (Greenfield) | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15
|  |  | IMC |  |  |  | 0.205 | 0.352 | 0.575 | 0.988 | 1.335 | 2.178 | 3.081 | 4.753 | 6.351 | 8.179 |  |  | 3/4" | [5 empty] | IMC |  |  |  | 0.181 | 0.311 | 0.508 | 0.873 | 1.179 | 1.924 | 2.722 | 4.199 | 5.61 | 7.224 |  |  | 1" |  |  | IMC |  |  |  | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 17 | IMC |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15
|  |  | LFNC-B (Carlon) |  |  | 0.115 | 0.188 | 0.325 | 0.524 | 0.917 | 1.188 | 1.948 | [6 empty] | 3/4" | [5 empty] | LFNC-B (Carlon) | 3: 0.102; 4: 0.166; 5: 0.287; 6: 0.462; 7: 0.81; 8: 1.05; 9: 1.72 |  | 1" |  |  | LFNC-B (Carlon) |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | [6 empty] | 9 | LFNC-B (Carlon) | 0 | 0 | 0 | 1 | 2 | 2 | 2 | [6 empty] | 7
|  |  | LFNC-A (Orange) |  |  | 0.115 | 0.187 | 0.321 | 0.513 | 0.901 | 1.211 | 2.006 | [6 empty] | 1" | [5 empty] | LFNC-A (Orange) | 3: 0.102; 4: 0.165; 5: 0.283; 6: 0.453; 7: 0.796; 8: 1.07; 9: 1.772 |  | 1" |  |  | LFNC-A (Orange) |  |  | 0 | 0 | 0 | 1 | 2 | 2 | 2 | [6 empty] | 7 | LFNC-A (Orange) | 0 | 0 | 0 | 1 | 2 | 2 | 2 | [6 empty] | 7
|  |  | LFMC (Sealtite) |  |  | 0.115 | 0.188 | 0.325 | 0.524 | 0.917 | 1.188 | 1.948 | 2.929 | 4.485 | 5.839 | 7.615 |  |  | 3/4" | [5 empty] | LFMC (Sealtite) |  |  | 0.102 | 0.166 | 0.287 | 0.462 | 0.81 | 1.05 | 1.72 | 2.587 | 3.962 | 5.158 | 6.727 |  |  | 1" |  |  | LFMC (Sealtite) |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 17 | LFMC (Sealtite) | 0 | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 15
|  |  | RMC (Rigid) |  |  |  | 0.188 | 0.329 | 0.532 | 0.916 | 1.243 | 2.045 | 2.919 | 4.499 | 6.006 | 7.729 | 12.127 | 17.495 | 3/4" | [5 empty] | RMC (Rigid) |  |  |  | 0.166 | 0.291 | 0.47 | 0.809 | 1.098 | 1.806 | 2.579 | 3.974 | 5.305 | 6.828 | 10.713 | 15.454 | 1" |  |  | RMC (Rigid) |  |  |  | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 21 | RMC (Rigid) |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19
|  |  | PVC (Schedule 80) |  |  |  | 0.13 | 0.246 | 0.413 | 0.742 | 1.027 | 1.725 | 2.471 | 3.865 | 5.213 | 6.755 | 10.713 | 15.359 | 1" | [5 empty] | PVC (Schedule 80) |  |  |  | 0.115 | 0.217 | 0.365 | 0.656 | 0.907 | 1.523 | 2.183 | 3.414 | 4.605 | 5.967 | 9.463 | 13.567 | 1" |  |  | PVC (Schedule 80) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19 | PVC (Schedule 80) |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19
|  |  | PVC (Schedule 40) |  |  |  | 0.171 | 0.305 | 0.499 | 0.872 | 1.191 | 1.975 | 2.817 | 4.361 | 5.842 | 7.532 | 11.856 | 17.14 | 1" | [5 empty] | PVC (Schedule 40) |  |  |  | 0.151 | 0.269 | 0.441 | 0.77 | 1.052 | 1.744 | 2.488 | 3.852 | 5.161 | 6.654 | 10.473 | 15.141 | 1" |  |  | PVC (Schedule 40) |  |  |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19 | PVC (Schedule 40) |  | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 19
|  |  | PVC (Type A) |  |  |  | 0.231 | 0.39 | 0.651 | 1.06 | 1.394 | 2.188 | 3.272 | 4.916 | 6.416 | 8.234 |  |  | 3/4" | [5 empty] | PVC (Type A) |  |  |  | 0.204 | 0.345 | 0.575 | 0.937 | 1.231 | 1.933 | 2.89 | 4.343 | 5.668 | 7.273 |  |  | 3/4" |  |  | PVC (Type A) |  |  |  | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 17 | PVC (Type A) |  | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  |  | 17
|  |  | PVC (Type EB) | [8 empty] | 2.325 |  | 5.226 | 6.819 | 8.669 | 13.317 | 18.918 | 3" | [5 empty] | PVC (Type EB) | 9: 2.053; 11: 4.616; 12: 6.023; 13: 7.657; 14: 11.763 | 16.711 | 3" |  |  | PVC (Type EB) | [8 empty] | 1 |  | 1 | 2 | 2 | 2 | 2 | 10 | PVC (Type EB) | [6 empty] | 1 |  | 1 | 2 | 2 | 2 | 2 | 10
Pipe (100% Fill)
|  |  | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6"
|  |  | EMT (Thinwall) |  |  |  | 0.304 | 0.533 | 0.864 | 1.496 | 2.036 | 3.356 | 5.858 | 8.846 | 11.545 | 14.753 |  |  | 0.864
|  |  | ENT (Smurf pipe) |  |  |  | 0.246 | 0.454 | 0.785 | 1.41 | 1.936 | 3.205 | [6 empty] | 0.785
|  |  | FMC (Greenfield) |  |  | 0.116 | 0.317 | 0.533 | 0.817 | 1.277 | 1.858 | 3.269 | 4.909 | 7.069 | 9.621 | 12.566 |  |  | 0.817
|  |  | IMC |  |  |  | 0.342 | 0.586 | 0.959 | 1.647 | 2.225 | 3.63 | 5.135 | 7.922 | 10.584 | 13.631 |  |  | 0.959
|  |  | LFNC-B (Carlon) |  |  | 0.192 | 0.314 | 0.541 | 0.873 | 1.528 | 1.981 | 3.246 | [6 empty] | 0.873
|  |  | LFNC-A (Orange) |  |  | 0.192 | 0.312 | 0.535 | 0.854 | 1.502 | 2.018 | 3.343 | [6 empty] | 0.854
|  |  | LFMC (Sealtite) |  |  | 0.192 | 0.314 | 0.541 | 0.873 | 1.528 | 0.981 | 3.246 | 4.881 | 7.475 | 9.731 | 12.692 |  |  | 0.873
|  |  | RMC (Rigid) |  |  |  | 0.314 | 0.549 | 0.887 | 1.526 | 2.071 | 3.408 | 4.866 | 7.499 | 10.01 | 12.882 | 20.212 | 29.158 | 0.887
|  |  | PVC (Schedule 80) |  |  |  | 0.217 | 0.409 | 0.688 | 1.237 | 1.711 | 2.874 | 4.119 | 6.442 | 8.688 | 11.258 | 17.855 | 25.598 | 0.688
|  |  | PVC (Schedule 40) |  |  |  | 0.285 | 0.508 | 0.832 | 1.453 | 1.986 | 3.291 | 4.695 | 7.268 | 9.737 | 12.554 | 19.761 | 28.567 | 0.832
|  |  | PVC (Type A) |  |  |  | 0.385 | 0.65 | 1.084 | 1.767 | 2.324 | 3.647 | 5.453 | 8.194 | 10.694 | 13.723 |  |  | 1.084
|  |  | PVC (Type EB) | [8 empty] | 3.824 |  | 8.709 | 11.365 | 14.448 | 22.195 | 31.53 | 0
Conductor Size Charts
Bare conductors, Insulated Conductors and Fixture Wires Area in Sq":
[24 empty] | AWG |  |  |  |  | 18 | 16 | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1 | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 400 | 500 | 600 | 700 | 750 | 800 | 900 | 1000 | 1250 | 1500 | 1750 | 2000
[24 empty] | BARE - Solid |  | 4: 0.001; 5: 0.002; 6: 0.003; 7: 0.005; 8: 0.008; 9: 0.013
[24 empty] | BARE - Stranded |  |  |  |  | 0.002 | 0.003 | 0.004 | 0.006 | 0.011 | 0.017 | 0.027 | 0.042 | 0.053 | 0.067 | 0.087 | 0.109 | 0.137 | 0.173 | 0.219 | 0.26 | 0.312 | 0.364 | 0.416 | 0.519 | 0.626 | 0.73 | 0.782 | 0.834 | 0.94 | 1.042 | 1.305 | 1.566 | 1.829 | 2.092
[24 empty] | BARE - [Compact Alum.] |  | 9: 0.0141; 10: 0.0224; 11: 0.0356; 13: 0.0564; 14: 0.0702 | 0.0887 | 0.1111 | 0.1406 | 0.1773 | 0.2125 | 0.2553 | 0.2981 | 0.3412 | 0.4256 | 0.5193 | 0.6043 | 0.6478 |  | 0.7856 | 0.8828
[24 empty] | THHN [Compact Alum.] |  | 10: 0.0452; 11: 0.073; 13: 0.1017; 14: 0.1352 | 0.159 | 0.1924 | 0.229 | 0.278 | 0.3525 | 0.4071 | 0.4656 | 0.5216 | 0.6151 | 0.762 | 0.8659 | 0.9076 |  | 1.1196 | 1.237
[24 empty] | THHW, THW [Compact Alum.] |  | 9: 0.051; 10: 0.066; 11: 0.0881; 13: 0.1194; 14: 0.1698 | 0.1963 | 0.2332 | 0.2733 | 0.3267 | 0.4128 | 0.4717 | 0.5281 | 0.5876 | 0.6939 | 0.8659 | 0.9676 | 1.0386 |  | 1.1766 | 1.2968
[24 empty] | XHHW [Compact Alum.] |  | 9: 0.0394; 10: 0.053; 11: 0.073; 13: 0.1017; 14: 0.1352 | 0.159 | 0.1885 | 0.229 | 0.2733 | 0.3421 | 0.4015 | 0.4536 | 0.5026 | 0.6082 | 0.7542 | 0.8659 | 0.9331 |  | 1.0733 | 1.1882
[24 empty] | FEP, FEPB |  | 6: 0.01; 7: 0.0137; 8: 0.0191; 9: 0.0333; 10: 0.0468; 11: 0.067; 12: 0.0804; 13: 0.0973
[24 empty] | PFA |  | 6: 0.01; 7: 0.0137; 8: 0.0191; 9: 0.0333; 10: 0.0468; 11: 0.067; 12: 0.0804; 13: 0.0973 | 0.1676 | 0.2027 | 0.2463 | 0.3
|  |  | Override Data | [20 empty] | PFAH, TFE | [6 empty] | 0.01 | 0.0137 | 0.0191 | 0.0333 | 0.0468 | 0.067 | 0.0804 | 0.0973 | 0.1399 | 0.1676 | 0.2027 | 0.2463 | 0.3
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | [9 empty] | RHH*, RHW*, RHW-2* without covering | [6 empty] | 0.0209 | 0.026 | 0.0333 | 0.0556 | 0.0726 | 0.0973 | 0.1134 | 0.1333 | 0.1901 | 0.2223 | 0.2624 | 0.3117 | 0.3718 | 0.4596 | 0.5281 | 0.5958 | 0.6619 | 0.7901 | 0.9729 | 1.101 | 1.1652 | 1.2272 | 1.3561 | 1.4784 | 1.8602 | 2.1695 | 2.4773 | 2.7818
|  |  | 1/2" | 1/2" | 3/8" | 1/2" | 3/8" | 3/8" | 3/8" | 1/2" | 1/2" | 1/2" | 1/2" | 2" | 1 |  | EMT (Thinwall) |  |  |  | 1/2" |  |  | RHH, RHW, RHW-2 with covering | [6 empty] | 0.0293 | 0.0353 | 0.0437 | 0.0835 | 0.1041 | 0.1333 | 0.1521 | 0.175 | 0.266 | 0.3039 | 0.3505 | 0.4072 | 0.4754 | 0.6291 | 0.7088 | 0.787 | 0.8626 | 1.0082 | 1.2135 | 1.3561 | 1.4272 | 1.4957 | 1.6377 | 1.7719 | 2.3479 | 2.6938 | 3.0357 | 3.3719
|  |  | 3/4" | 3/4" | 1/2" | 3/4" | 1/2" | 1/2" | 1/2" | 3/4" | 3/4" | 3/4" | 3/4" | 3" | 1 |  | EMT (Thinwall) |  |  |  | 3/4" |  |  | THHN, THWN, THWN-2 | [6 empty] | 0.0097 | 0.0133 | 0.0211 | 0.0366 | 0.0507 | 0.0824 | 0.0973 | 0.1158 | 0.1562 | 0.1855 | 0.2223 | 0.2679 | 0.3237 | 0.397 | 0.4608 | 0.5242 | 0.5863 | 0.7073 | 0.8676 | 0.9887 | 1.0496 | 1.1085 | 1.2311 | 1.3478
|  |  | 1" | 1" | 3/4" | 1" | 3/4" | 3/4" | 3/4" | 1" | 1" | 1" | 1" | 3 1/2" | 2 |  | ENT (Smurf pipe) |  |  |  | 1" |  |  | THW, THW-2, THHW, TW | [6 empty] | 0.0139 | 0.0181 | 0.0243 | 0.0437 | 0.0726 | 0.0973 | 0.1134 | 0.1333 | 0.1901 | 0.2223 | 0.2624 | 0.3117 | 0.3718 | 0.4596 | 0.5281 | 0.5958 | 0.6619 | 0.7901 | 0.9729 | 1.101 | 1.1652 | 1.2272 | 1.3561 | 1.4784 | 1.8602 | 2.1695 | 2.4773 | 2.7818
|  |  | 1 1/4" | 1 1/4" | 1" | 1 1/4" | 1" | 1" | 1" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/4" | 4" | 3 |  | FMC (Greenfield) |  |  |  | 1 1/4" |  |  | XHH, XHHW, XHHW-2 | [6 empty] | 0.0139 | 0.0181 | 0.0243 | 0.0437 | 0.059 | 0.0814 | 0.0962 | 0.1146 | 0.1534 | 0.1825 | 0.219 | 0.2642 | 0.3197 | 0.3904 | 0.4536 | 0.5166 | 0.5782 | 0.6984 | 0.8709 | 0.9923 | 1.0532 | 1.1122 | 1.2351 | 1.3519 | 1.718 | 2.0157 | 2.3127 | 2.6073
|  |  | 1 1/2" | 1 1/2" | 1 1/4" | 1 1/2" | 1 1/4" | 1 1/4" | 1 1/4" | 1 1/2" | 1 1/2" | 1 1/2" | 1 1/2" | 5" | 4 |  | IMC |  |  |  | 1 1/2" |  |  | Z | [6 empty] | 0.0083 | 0.0117 | 0.0191 | 0.0302 | 0.043 | 0.0625 | 0.0855 | 0.1029 | 0.1269 | 0.1676 | 0.2027 | 0.2463 | 0.3
|  |  | 2" | 2" | 1 1/2" | 2" | 1 1/2" | 1 1/2" | 1 1/2" | 2" | 2" | 2" | 2" | 6" | 5 |  | LFNC-B (Carlon) |  |  |  | 2" |  |  | ZW |  | 6: 0.0139; 7: 0.0181; 8: 0.0243; 9: 0.0437; 10: 0.059; 11: 0.0814; 12: 0.0962; 13: 0.1146
|  |  | 2 1/2" |  | 2" | 2 1/2" | 2" | 2" | 2" | 2 1/2" | 2 1/2" | 2 1/2" | 2 1/2" |  | 6 |  | LFNC-A (Orange) |  |  |  | 2 1/2" |  |  | FFH-2, RFH-2 |  | 4: 0.0145; 5: 0.0172
|  |  | 3" |  | 2 1/2" | 3" |  |  | 2 1/2" | 3" | 3" | 3" | 3" |  | 7 |  | LFMC (Sealtite) |  |  |  | 3" |  |  | KF-1, KFF-1 |  | 4: 0.0026; 5: 0.0037; 6: 0.0055; 7: 0.0083; 8: 0.0127
|  |  | 3 1/2" |  | 3" | 3 1/2" |  |  | 3" | 3 1/2" | 3 1/2" | 3 1/2" | 3 1/2" |  | 8 |  | RMC (Rigid) |  |  |  | 3 1/2" |  |  | KF-2, KFF-2 |  | 4: 0.0031; 5: 0.0044; 6: 0.0064; 7: 0.0093; 8: 0.0139
|  |  | 4" |  | 3 1/2" | 4" |  |  | 3 1/2" | 4" | 4" | 4" | 4" |  | 9 |  | PVC (Schedule 80) |  |  |  | 4" |  |  | PAF, PAFF, PF, PFF |  | 4: 0.0058; 5: 0.0075; 6: 0.001
[5 empty] | 4" |  |  |  | 4" | 5" | 5" | 5" |  |  | 10 |  | PVC (Schedule 40) | [6 empty] | PGF, PGFF, PTF, PTFF |  | 4: 0.0058; 5: 0.0075; 6: 0.001
[10 empty] | 6" | 6" | 6" |  |  | 11 |  | PVC (Type A) | [6 empty] | RFH-1 |  | 4: 0.008
[15 empty] | 12 |  | PVC (Type EB) | [6 empty] | SF-1, SFF-1 |  | 4: 0.0065
[24 empty] | SF-2, SFF-2 |  | 4: 0.0115; 5: 0.0139; 6: 0.0172
[24 empty] | TF, TFF |  | 5: 0.0109
[24 empty] | TFN, TFFN |  | 4: 0.0055; 5: 0.0072
[24 empty] | XF, XFF |  | 4: 0.008; 5: 0.0109; 6: 0.0139; 7: 0.026; 8: 0.0333
[24 empty] | ZF, ZFF |  | 4: 0.0045; 5: 0.0061; 6: 0.0083
* Types RHH*, RHW*, and RHW-2* without overall covering
Note: This information was compiled using the 2011 NEC from Tables 4,5 and 8 of chapter 9.
|  |  | Conduit Diameter Size Charts | [20 empty] | Conductor Diameter Charts used for Jamming
Conduit inside diameters used for jamming
|  |  | Conduit Sizes: |  |  | 3/8" | 1/2" | 3/4" | 1" | 1 1/4" | 1 1/2" | 2" | 2 1/2" | 3" | 3 1/2" | 4" | 5" | 6" | [5 empty] | AWG |  |  |  |  | 18 | 16 | 14 | 12 | 10 | 8 | 6 | 4 | 3 | 2 | 1 | 1/0 | 2/0 | 3/0 | 4/0 | 250 | 300 | 350 | 400 | 500 | 600 | 700 | 750 | 800 | 900 | 1000 | 1250 | 1500 | 1750 | 2000
|  |  | EMT (Thinwall) |  |  |  | 0.622 | 0.824 | 1.049 | 1.38 | 1.61 | 2.067 | 2.731 | 3.356 | 3.834 | 4.334 | [7 empty] | BARE - Solid |  | 4: 0.04; 5: 0.051; 6: 0.064; 7: 0.081; 8: 0.102; 9: 0.128
|  |  | ENT (Smurf pipe) |  |  |  | 0.56 | 0.76 | 1 | 1.34 | 1.57 | 2.02 | [11 empty] | BARE - Stranded |  |  |  |  | 0.046 | 0.058 | 0.073 | 0.092 | 0.116 | 0.146 | 0.184 | 0.232 | 0.26 | 0.292 | 0.332 | 0.372 | 0.418 | 0.47 | 0.528 | 0.575 | 0.63 | 0.681 | 0.728 | 0.813 | 0.893 | 0.964 | 0.998 | 1.03 | 1.094 | 1.152 | 1.289 | 1.412 | 1.526 | 1.632
|  |  | FMC (Greenfield) |  |  | 0.384 | 0.635 | 0.824 | 1.02 | 1.275 | 1.538 | 2.04 | 2.5 | 3 | 3.5 | 4 | [7 empty] | BARE - [Compact Alum.] |  | 9: 0.134; 10: 0.169; 11: 0.213; 13: 0.268; 14: 0.299 | 0.336 | 0.376 | 0.423 | 0.475 | 0.52 | 0.57 | 0.616 | 0.659 | 0.736 | 0.813 | 0.877 | 0.908 |  | 0.999 | 1.06
|  |  | IMC |  |  |  | 0.66 | 0.864 | 1.105 | 1.448 | 1.683 | 2.15 | 2.557 | 3.176 | 3.671 | 4.166 | [7 empty] | THHN [Compact Alum.] |  | 10: 0.24; 11: 0.305; 13: 0.36; 14: 0.415 | 0.45 | 0.495 | 0.54 | 0.595 | 0.67 | 0.72 | 0.77 | 0.815 | 0.885 | 0.985 | 1.05 | 1.075 |  | 1.194 | 1.255
|  |  | LFNC-B (Carlon) |  |  | 0.494 | 0.632 | 0.83 | 1.054 | 1.395 | 1.588 | 2.033 | [11 empty] | THHW, THW [Compact Alum.] |  | 9: 0.255; 10: 0.29; 11: 0.335; 13: 0.39; 14: 0.465 | 0.5 | 0.545 | 0.59 | 0.645 | 0.725 | 0.775 | 0.82 | 0.865 | 0.94 | 1.05 | 1.11 | 1.15 |  | 1.224 | 1.285
|  |  | LFNC-A (Orange) |  |  | 0.495 | 0.63 | 0.825 | 1.043 | 1.383 | 1.603 | 2.063 | [11 empty] | XHHW [Compact Alum.] |  | 9: 0.224; 10: 0.26; 11: 0.305; 13: 0.36; 14: 0.415 | 0.45 | 0.49 | 0.54 | 0.59 | 0.66 | 0.715 | 0.76 | 0.8 | 0.88 | 0.98 | 1.05 | 1.09 |  | 1.169 | 1.23
|  |  | LFMC (Sealtite) |  |  | 0.494 | 0.632 | 0.83 | 1.054 | 1.395 | 1.588 | 2.033 | 2.493 | 3.085 | 3.52 | 4.02 | [7 empty] | FEP, FEPB |  | 6: 0.113; 7: 0.132; 8: 0.156; 9: 0.206; 10: 0.244; 11: 0.292; 12: 0.32; 13: 0.352
|  |  | RMC (Rigid) |  |  |  | 0.632 | 0.836 | 1.063 | 1.394 | 1.624 | 2.083 | 2.489 | 3.09 | 3.57 | 4.05 | 5.073 | 6.093 | [5 empty] | PFA |  | 6: 0.113; 7: 0.132; 8: 0.156; 9: 0.206; 10: 0.244; 11: 0.292; 12: 0.32; 13: 0.352 | 0.462 | 0.508 | 0.56 | 0.618
|  |  | PVC (Schedule 80) |  |  |  | 0.526 | 0.722 | 0.936 | 1.255 | 1.476 | 1.913 | 2.29 | 2.864 | 3.326 | 3.786 | 4.768 | 5.709 | [5 empty] | PFAH, TFE | [6 empty] | 0.113 | 0.132 | 0.156 | 0.206 | 0.244 | 0.292 | 0.32 | 0.352 | 0.422 | 0.462 | 0.508 | 0.56 | 0.618
|  |  | PVC (Schedule 40) |  |  |  | 0.602 | 0.804 | 1.029 | 1.36 | 1.59 | 2.047 | 2.445 | 3.042 | 3.521 | 3.998 | 5.016 | 6.031 | [5 empty] | RHH*, RHW*, RHW-2* without covering | [6 empty] | 0.193 | 0.212 | 0.236 | 0.326 | 0.364 | 0.412 | 0.44 | 0.472 | 0.582 | 0.622 | 0.668 | 0.72 | 0.778 | 0.895 | 0.95 | 1.001 | 1.048 | 1.133 | 1.243 | 1.314 | 1.348 | 1.38 | 1.444 | 1.502 | 1.729 | 1.852 | 1.966 | 2.072
|  |  | PVC (Type A) |  |  |  | 0.7 | 0.91 | 1.175 | 1.5 | 1.72 | 2.155 | 2.635 | 3.23 | 3.69 | 4.18 | [7 empty] | RHH, RHW, RHW-2 with covering | [6 empty] | 0.163 | 0.182 | 0.206 | 0.266 | 0.304 | 0.352 | 0.38 | 0.412 | 0.492 | 0.532 | 0.578 | 0.63 | 0.688 | 0.765 | 0.82 | 0.871 | 0.918 | 1.003 | 1.113 | 1.184 | 1.218 | 1.25 | 1.314 | 1.372 | 1.539 | 1.662 | 1.776 | 1.882
|  |  | PVC (Type EB) | [8 empty] | 2.221 |  | 3.33 | 3.804 | 4.289 | 5.316 | 6.336 | [5 empty] | THHN, THWN, THWN-2 | [6 empty] | 0.111 | 0.13 | 0.164 | 0.216 | 0.254 | 0.324 | 0.352 | 0.384 | 0.446 | 0.486 | 0.532 | 0.584 | 0.642 | 0.711 | 0.766 | 0.817 | 0.864 | 0.949 | 1.051 | 1.122 | 1.156 | 1.188 | 1.252 | 1.31
[24 empty] | THW, THW-2, THHW, TW | [6 empty] | 0.133 | 0.152 | 0.176 | 0.236 | 0.304 | 0.352 | 0.38 | 0.412 | 0.492 | 0.532 | 0.578 | 0.63 | 0.688 | 0.765 | 0.82 | 0.871 | 0.918 | 1.003 | 1.113 | 1.184 | 1.218 | 1.25 | 1.314 | 1.372 | 1.539 | 1.662 | 1.776 | 1.882
[24 empty] | XHH, XHHW, XHHW-2 | [6 empty] | 0.133 | 0.152 | 0.176 | 0.236 | 0.274 | 0.322 | 0.35 | 0.382 | 0.442 | 0.482 | 0.528 | 0.58 | 0.638 | 0.705 | 0.76 | 0.811 | 0.858 | 0.943 | 1.053 | 1.124 | 1.158 | 1.19 | 1.254 | 1.312 | 1.479 | 1.602 | 1.716 | 1.822
[24 empty] | Z | [6 empty] | 0.103 | 0.122 | 0.156 | 0.196 | 0.234 | 0.282 | 0.33 | 0.362 | 0.402 | 0.462 | 0.508 | 0.56 | 0.618
[24 empty] | ZW |  | 6: 0.133; 7: 0.152; 8: 0.176; 9: 0.236; 10: 0.274; 11: 0.322; 12: 0.35; 13: 0.382
[24 empty] | FFH-2, RFH-2 |  | 4: 0.136; 5: 0.148
[24 empty] | KF-1, KFF-1 |  | 4: 0.057; 5: 0.069; 6: 0.084; 7: 0.103; 8: 0.127
[24 empty] | KF-2, KFF-2 |  | 4: 0.063; 5: 0.075; 6: 0.09; 7: 0.109; 8: 0.133
[24 empty] | PAF, PAFF, PF, PFF |  | 4: 0.086; 5: 0.098; 6: 0.113
[24 empty] | PGF, PGFF, PTF, PTFF |  | 4: 0.086; 5: 0.098; 6: 0.113
[24 empty] | RFH-1 |  | 4: 0.106
[24 empty] | SF-1, SFF-1 |  | 4: 0.091
[24 empty] | SF-2, SFF-2 |  | 4: 0.121; 5: 0.133; 6: 0.148
[24 empty] | TF, TFF |  | 5: 0.118
[24 empty] | TFN, TFFN |  | 4: 0.084; 5: 0.096
[24 empty] | XF, XFF |  | 4: 0.106; 5: 0.118; 6: 0.133; 7: 0.182; 8: 0.206
[24 empty] | ZF, ZFF |  | 4: 0.076; 5: 0.088; 6: 0.103

## Residential Wiring Course
" WireLab - A Residential Wiring Course" is the latest product of WireLab Services. The
software was written in Visual Basic by Bobby Bamford, an electrical engineer in Orlando,
Fla. The text book was written by his twin brother Bill Bamford, a state licensed electrician
in Albany, Ga, who taught electrical classes in a Technical College for 8 years.
For further information contact either: Bobby_Bamford@Yahoo.com or Bill_Bamford @ Yahoo.com www.wirelabservices.com
A Residential Wiring Course by Wirelab Services
WireLab is a residential wiring course which utilizes both textbook and software to teach residential wiring to students in Electrical Classes. The software is only
available to students in schools which purchase a three year site license. The software is downloaded onto a jump drive so that the student can use it at his convience
on any PC. The textbook has 17 chapters covering all aspects of house wiring with an assignment in the software for each chapter's topic. The student will wire a
complete house on the computer. Each chapter progresses through the steps of roughing in and trimming out a house. As each assignment is completed, the software
checks the student's work. If any faults are found, the errors are reported. Any codes that are violated can be viewed. The student works through the reported error list
until he is able to pass the assignment. He then reads the next chapter and then works another assingment in the software. The student must also complete lab work
at school. This course does not eliminate the need for hands on training. It teaches what to do. Labs teach how to do it. If a student knows which size boxes, wires and
panels to use, then teaching the student how to install them and to the make connections becomes easy. The floorplan below is wired by the student as he reads
through the textbook. Many other floor plans are available for wiring. The software also has tools which can be used to create new floor plans and then to check them for
code violations. The software and book are updated for the latest codes every three years. If you know of any school which may be interested in this software, please let
us know. We will be glad to send them information and pricing on the course. The drawings on the following pages are samples from the software.
Panels must be wired, with proper breaker selection |  |  |  | Sample trim-out inspection |  |  | All receptacles, switches, lights, and appliances must be wired
Each cable wire in the panel must be pulled to the appropriate
ground bar, neutral bar or breaker. The main bonding jumper
must also be installed, if required. Once the panel is wired, the
power can be turned on. Then each main breaker, branch circuit
breaker or switch can be toggled to turn on and off any ceiling
fans, lights, receptacles, appliances, etc.
When a breaker in the panel is selected, the entire branch circuit is highlighted in blue lines | [5 empty] | When a cable is selected in a device box, the cable is highlighted in blue and the box
on the floor plan. |  | (Notice the cursor on breaker #1) |  |  |  | is circled. |  |  | (Notice the cursor on the third cable from left)
When a cable is dragged from box to box on the floorplan, the cable ends become visible inside
the boxes, fixtures, appliances and panels. Then the student drags the ends of each conductor
to the appropriate terminal. Then a trimout test is requested. The software presents an interactive
report that explains any errors found. The student corrects the error and reruns the trimout test.
until all tests pass. After the building is wired, the power can be turned on, and all switches and
breakers can be toggled to view the results on screen.
Table of Contents:
I. Introduction
The WireLab Textbook |  |  | I. Roughing-in the house
1. Installing Service and Panel Enclosures
2. Installing Receptacle Boxes
3. Installing Swtich and Lighting Fixture Boxes
4. Installing Appliance Enclosures
5. Installing Service and Feeder Cables
6. Installing Branch Circuit Cables
7. Installing Cables for Restricted Branch Circuits
8. Installing Cables for Switches and Fixtures
9. Installing Cables for Appliances
10. Finishing up the Rough-in
II. Trimming-Out the House
11. Wiring Receptacles
12. Wiring Single Pole Switches
13. Wiring 3-Way and 4-Way Switches
14. Wiring Fixtures and Ceiling Fans
15. Wiring Appliances
16. Wiring Services and Subpanels
17. Finishing up the Trim-out
III Appendix
A. Voltage and Current
B. Grounding Equipment and Buildings
C. Wire Sizing
D. Box Sizing (Box Fill Calculations)
|  |  | E. Tools of the Trade |  |  |  |  | The illustration above shows a branch circuit that has all lights wired hot.
|  |  | F. International Building Codes on Drilling and Notching Wood |  |  |  |  | The 2011 NEC requires the use of four conductor cables for 3-way and
|  |  | G. The Functioning of GFCI |  |  |  |  | 4-way switches wired this way in order to meet the new code requiring
|  |  | H. The Functioning of AFCI |  |  |  |  | a neutral conductor in every switch box for future use [NEC 404.2 (C)].
|  |  | I. WirLab's Rough-in and Trim-out Inspections |  |  |  |  | This illustration is in Chapter 13 for wiring 3-way and 4-way switches.
|  |  | J. Definitions and Abbreviations |  |  |  |  | The WireLab software allows the user to waive this requirement if he is
|  |  | K. NEC Residential Code Changes |  |  |  |  | in a jurisdiction that does not adopt this new code.
L House 1 Assignments
Wirelab