## Copper Voltage Drop
Enter values in yellow boxes (only!) for automatic Copper AC voltage drop calculation | [13 empty] | Table | Table
Three Phase Three-Wire Circuits | [13 empty] | Wire size | (circ. Mills)
Drop (30°C) = 2K x L x I X 0.866 = |  |  | 25.8 | x | 0 | x | 0 | X | 0.866 | = | 0 | volts drop | 0% | 18/ | 1620 | AWG
| D |  |  |  | 0 | [8 empty] | 16/ | 2580 | AWG
K = Conductor resistivity = 12.9 for >50% ampacity & 11 for <50% ampacity copper, L = One way length of conductors in feet, | [13 empty] | 14/ | 4110 | AWG
I = Device(s) total rated current in amps | [13 empty] | 12/ | 6530 | AWG
Enter wire size (with slash) (ie. 12/, 1/, 2/0, 500/ - see Table) | [13 empty] | 10/ | 10380 | AWG
D = Conductor cross section (Automatically inserted) | [6 empty] | 0 | cm | [5 empty] | 8/ | 16510 | AWG
One way length of conductors in feet = | [7 empty] | ft | [5 empty] | 6/ | 26240 | AWG
Total full load circuit current = | [7 empty] | A | [5 empty] | 4/ | 41740 | AWG
Circuit Voltage = | [7 empty] | V | [5 empty] | 3/ | 52620 | AWG
[14 empty] | 2/ | 66360 | AWG
Single Phase Two-Wire Circuits | [13 empty] | 1/ | 83690 | AWG
Drop (30°C) = 2K x L x I = |  |  | 25.8 | x | 0 | x | 0 |  |  | = | 0 | volts drop | 0% | 1/0 | 105600 | AWG
| D |  |  |  | 0 | [8 empty] | 2/0 | 133100 | AWG
K = Conductor resistivity = 12.9 for >50% ampacity & 11 for <50% ampacity copper, L = Twice conduit run in feet ( 2 current carrying conductors in conduit) | [13 empty] | 3/0 | 167800 | AWG
I = Device(s) total rated current in amps | [13 empty] | 4/0 | 211600 | AWG
Enter size of wire to be used (ie. 12, 1, 2/0, 500 - see Table) | [13 empty] | 250/ | 250000 | (MCM) AWG
D = Conductor cross section (Automatically inserted from Table) | [6 empty] | 0 | cm | [5 empty] | 350/ | 350000 | (MCM) AWG
Two times length of conductor in feet (length of 2 conductors) = | [7 empty] | ft | [5 empty] | 500/ | 500000 | (MCM) AWG
Total full load circuit current = | [7 empty] | A | [5 empty] | 750/ | 750000 | (MCM) AWG
Circuit Voltage = | [7 empty] | V
Athough the NEC allows up to 3% votlage drop in a branch circuit, recommended practice is to design for no more than 1% voltage drop at full load on branch circuits
feeding sensitive equipment. Feeder circuits should not exceed 2% voltage drop. This results in a 5% voltage drop (2%+3%) from feeder to load.
°F Temperature Correction Ampere Capacity Derating Percentages
|  | FEPW, RH, RHW, THHW, |  |  |  |  | TA, TBS, SA, SIS, FEP, FEBP, MI, RHH, RHW-2
°F Ambient |  | THW, THWN, XHHW, ZW, |  |  |  |  | THHN, THHW, THW-2, THWN-2, USE-2, XHH,
Temperature | TW, UF Rated Wire | USE Rated Wire |  |  |  |  | XHHW, XHHW-2, ZW-2 Rated Wire | [6 empty] | by: Tom Moss
88-95 | 91% | 94% |  |  |  |  | 96%
96-104 | 82% | 88% |  |  |  |  | 91%
105-113 | 71% | 82% |  |  |  |  | 87%
114-122 | 58% | 75% |  |  |  |  | 82%
123-131 | 41% | 67% |  |  |  |  | 76%
132-140 | N/A | 58% |  |  |  |  | 71%
141-158 | N/A | 33% |  |  |  |  | 58%
159-176 | N/A | N/A |  |  |  |  | 41%

## Aluminum Voltage Drop
Enter values in yellow boxes (only!) for automatic Aluminum AC voltage drop calculation | [13 empty] | Table | Table
Three Phase Three-Wire Circuits | [13 empty] | Wire size | (circ. Mills)
Drop (30°C) = 2K x L x I X 0.866 = |  |  | 42.4 | x | 0 | x | 0 | X | 0.866 | = | 0 | volts drop | 0% | 18/ | 1620 | AWG
| D |  |  |  |  | 0 | [7 empty] | 16/ | 2580 | AWG
K = Resistivity of conductor = 21.2 |  | L = One way length of conductors in feet | [11 empty] | 14/ | 4110 | AWG
I = Device(s) total rated current in amps | [13 empty] | 12/ | 6530 | AWG
Enter wire size (with slash) (ie. 12/, 1/, 2/0, 500/ - see Table) | [13 empty] | 10/ | 10380 | AWG
D = Conductor cross section (Automatically inserted) | [6 empty] | 0 | cm | [5 empty] | 8/ | 16510 | AWG
One way length of conductors in feet = | [7 empty] | ft | [5 empty] | 6/ | 26240 | AWG
Total full load circuit current = | [7 empty] | A | [5 empty] | 4/ | 41740 | AWG
Circuit Voltage = | [7 empty] | V | [5 empty] | 3/ | 52620 | AWG
[14 empty] | 2/ | 66360 | AWG
Single Phase Two-Wire Circuits | [13 empty] | 1/ | 83690 | AWG
Drop (30°C) = 2K x L x I = |  |  | 42.4 | x | 0 | x | 0 |  |  | = | 0 | volts drop | 0% | 1/0 | 105600 | AWG
| D |  |  |  |  | 0 | [7 empty] | 2/0 | 133100 | AWG
K = Conductor resistivity = 21.2, L = Twice conduit run in feet ( 2 current carrying conductors in conduit) | [13 empty] | 3/0 | 167800 | AWG
I = Device(s) total rated current in amps | [13 empty] | 4/0 | 211600 | AWG
Enter size of wire to be used (ie. 12, 1, 2/0, 500 - see Table) | [13 empty] | 250/ | 250000 | (MCM) AWG
D = Conductor cross section (Automatically inserted from Table) | [6 empty] | 0 | cm | [5 empty] | 350/ | 350000 | (MCM) AWG
Two times length of conductor in feet (length of 2 conductors) = | [7 empty] | ft | [5 empty] | 500/ | 500000 | (MCM) AWG
Total full load circuit current = | [7 empty] | A | [5 empty] | 750/ | 750000 | (MCM) AWG
Circuit Voltage = | [7 empty] | V
Athough the NEC allows up to 3% votlage drop in a branch circuit, recommended practice is to design for no more than 1% voltage drop at full load on branch circuits
feeding sensitive equipment. Feeder circuits should not exceed 2% voltage drop. This results in a 5% voltage drop (2%+3%) from feeder to load.
°F Temperature Correction Ampere Capacity Derating Percentages
|  | FEPW, RH, RHW, THHW, |  |  |  |  | TA, TBS, SA, SIS, FEP, FEBP, MI, RHH, RHW-2
°F Ambient |  | THW, THWN, XHHW, ZW, |  |  |  |  | THHN, THHW, THW-2, THWN-2, USE-2, XHH,
Temperature | TW, UF Rated Wire | USE Rated Wire |  |  |  |  | XHHW, XHHW-2, ZW-2 Rated Wire
88-95 | 91% | 94% |  |  |  |  | 96%
96-104 | 82% | 88% |  |  |  |  | 91%
105-113 | 71% | 82% |  |  |  |  | 87%
114-122 | 58% | 75% |  |  |  |  | 82%
123-131 | 41% | 67% |  |  |  |  | 76%
132-140 | N/A | 58% |  |  |  |  | 71%
141-158 | N/A | 33% |  |  |  |  | 58%
159-176 | N/A | N/A |  |  |  |  | 41%