## Ampacity
|  |  | Copper | 1/phase | 2/phase | 3/phase | 4/phase | 5/phase | 6/phase | 7/phase | 8/phase | 1/phase | 2/phase | 3/phase | 4/phase | 5/phase | 6/phase | 7/phase | 8/phase
INPUTS |  |  |  | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | Use | Use | Use | Use | Use | Use | Use | Use
Load | 1200 | Design Load |  | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor
Continuous? (y/n) | N | 1200 |  | Over | 1500 | 600 | 350 | 250 | 3/0 | 2/0 | 1/0 | 750 | 600 | 600 | 350 | 250 | 3/0 | 2/0 | 1/0
Ambient Temperature - C | 30 | 1 |  |  | 1500000 | 600000 | 350000 | 250000 | 167800 | 133100 | 105600 | 750000 | 600000 | 600000 | 350000 | 250000 | 167800 | 133100 | 105600
Ambient Temperature - F |  |  |  | 90degC | 90degC | 90degC | 90degC | 90degC | 90degC | 90degC | 90degC
Current Carrying Conductors | 3 | 1 |  | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor
| OCP size | 1200 |  | Over | 1000 | 500 | 300 | 4/0 | 3/0 | 2/0 | 1/0
| 1200 |  |  |  | 1000000 | 500000 | 300000 | 211600 | 167800 | 133100 | 105600
|  | EGC |  | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond.
Voltage Drop |  | 3/0 |  | Over | 1500 | 600 | 350 | 250 | 3/0 | 2/0 | 1/0
Number of Phases | 3 |  |  |  | 1500000 | 600000 | 350000 | 250000 | 167800 | 133100 | 105600
Raceway type | Steel |  | tot kcmil | 0 | 3000000 | 1800000 | 1400000 | 1250000 | 1006800 | 931700 | 844800 |  |  | 1800000 | 1400000 | 1250000 | 1006800 | 931700 | 844800 | tot kcmil
Power Factor | 95 |  | X |  |  | 0.048 | 0.05 | 0.052 | 0.052 | 0.054 | 0.055 |  |  | 0.048 | 0.05 | 0.052 | 0.052 | 0.054 | 0.055 | X
System Voltage | 480 |  | R |  |  | 0.025 | 0.039 | 0.054 | 0.079 | 0.1 | 0.12 |  |  | 0.025 | 0.039 | 0.054 | 0.079 | 0.1 | 0.12 | R
2% Voltage drop | 9.6 |  | Zeff |  |  | 0.038738 | 0.052662 | 0.067537 | 0.091287 | 0.11186 | 0.13117 |  |  | 0.038738 | 0.052662 | 0.067537 | 0.091287 | 0.11186 | 0.13117 | Zeff
3% Voltage drop | 14.4 |  | Vd/kf |  |  | 26.8385 | 27.3642 | 28.0746 | 31.6227 | 33.2143 | 34.0799 |  |  | 26.8385 | 27.3642 | 28.0746 | 31.6227 | 33.2143 | 34.0799 | Vd/kf
|  |  | 2% dist |  |  | 357.6955 | 350.8229 | 341.9461 | 303.579 | 289.0326 | 281.6906 |  |  | 357.6955 | 350.8229 | 341.9461 | 303.579 | 289.0326 | 281.6906 | 2% dist
|  |  | 3% dist |  |  | 536.5432 | 526.2343 | 512.9191 | 455.3685 | 433.5489 | 422.536 |  |  | 536.5432 | 526.2343 | 512.9191 | 455.3685 | 433.5489 | 422.536 | 3% dist
cos(theta) | 0.95 |  | TrueK |  |  | 23.2428 | 18.4319 | 16.8842 | 15.318 | 14.8888 | 13.8519 |  |  | 23.2428 | 18.4319 | 16.8842 | 15.318 | 14.8888 | 13.8519 | TrueK
sin(theta) | 0.31225 |  | KID 2% |  | 1074.14 | 644.484 | 501.2653 | 447.5583 | 360.4814 | 333.5921 | 302.4778 |  |  | 644.484 | 501.2653 | 447.5583 | 360.4814 | 333.5921 | 302.4778 | KID 2%
|  |  | KID 3% |  | 1611.2101 | 966.726 | 751.898 | 671.3375 | 540.7221 | 500.3881 | 453.7168 |  |  | 966.726 | 751.898 | 671.3375 | 540.7221 | 500.3881 | 453.7168 | KID 3%
|  |  | Aluminum |  | 2/phase | 3/phase | 4/phase | 5/phase | 6/phase | 7/phase | 8/phase | 1/phase | 2/phase | 3/phase | 4/phase | 5/phase | 6/phase | 7/phase | 8/phase
|  |  |  | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | 75°C Termination | Use | Use | Use | Use | Use | Use | Use | Use
|  |  |  | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor size | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor
|  |  |  | Over | Over | 900 | 500 | 350 | 250 | 4/0 | 3/0 | 750 | 250 | 1000 | 600 | 500 | 350 | 250 | 4/0
[6 empty] | 900000 | 500000 | 350000 | 250000 | 211600 | 167800 | 750000 | 250000 | 1000000 | 600000 | 500000 | 350000 | 250000 | 211600
|  |  |  | 90°C adjusted | 90°C adjusted | 90°C adjusted | 90°C adjusted | 90°C adjusted | 90°C adjusted | 90°C adjusted | 90°C adjusted
|  |  |  | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor | Conductor
|  |  |  | Over | 1750 | 700 | 400 | 300 | 4/0 | 3/0 | 2/0
[5 empty] | 1750000 | 700000 | 400000 | 300000 | 211600 | 167800 | 133100
|  | EGC |  | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond. | Use Cond.
|  | 250 |  | Over | Over | 900 | 500 | 350 | 250 | 4/0 | 3/0
[6 empty] | 900000 | 500000 | 350000 | 250000 | 211600 | 167800
|  |  | tot kcmil | 0 | 0 | 2700000 | 2000000 | 1750000 | 1500000 | 1481200 | 1342400 |  |  | 3000000 | 2400000 | 2500000 | 2100000 | 1750000 | 1692800 | tot kcmil
|  |  | X |  |  |  | 0.048 | 0.05 | 0.052 | 0.051 | 0.052 |  |  | 0.046 | 0.048 | 0.048 | 0.05 | 0.052 | 0.051 | X
|  |  | R |  |  |  | 0.045 | 0.063 | 0.086 | 0.1 | 0.13 |  |  | 0.025 | 0.038 | 0.045 | 0.063 | 0.086 | 0.1 | R
|  |  | Zeff |  |  |  | 0.057738 | 0.075462 | 0.097937 | 0.11092 | 0.13974 |  |  | 0.038113 | 0.051088 | 0.057738 | 0.075462 | 0.097937 | 0.11092 | Zeff
|  |  | Vd/kf |  |  |  | 30.0015 | 31.3692 | 33.9264 | 32.9361 | 36.3047 |  |  | 26.4058 | 26.5461 | 24.0012 | 26.141 | 29.0797 | 28.8191 | Vd/kf
|  |  | 2% dist |  |  |  | 319.9835 | 306.033 | 282.9657 | 291.4734 | 264.4283 |  |  | 363.5564 | 361.635 | 399.9794 | 367.2396 | 330.1267 | 333.1125 | 2% dist
|  |  | 3% dist |  |  |  | 479.9753 | 459.0494 | 424.4486 | 437.2101 | 396.6425 |  |  | 545.3347 | 542.4525 | 599.9692 | 550.8593 | 495.19 | 499.6687 | 3% dist
|  |  | TrueK |  |  |  | 28.869 | 26.4119 | 24.4842 | 23.4717 | 23.4479 |  |  | 38.1135 | 30.6528 | 28.869 | 26.4119 | 24.4842 | 23.4717 | TrueK
|  |  | Kid 2% |  |  | 588.2437 | 435.7361 | 381.269 | 326.802 | 322.7061 | 292.466 |  |  | 653.6041 | 522.8833 | 544.6701 | 457.5229 | 381.269 | 368.807 | Kid 2%
|  |  | Kid 3% |  |  | 882.3655 | 653.6041 | 571.9036 | 490.2031 | 484.0592 | 438.6991 |  |  | 980.4061 | 784.3249 | 817.0051 | 686.2843 | 571.9036 | 553.2105 | Kid 3%
Note on D15: Eric Stromberg: This is the X value for a single conductor, straight from the table
Note on V15: Eric Stromberg: This is the X value for a single conductor, straight from the table
Note on D16: Eric Stromberg: This is the R value for a single conductor, straight from the table
Note on V16: Eric Stromberg: This is the R value for a single conductor, straight from the table
Note on D17: Eric Stromberg: This is the calcuated Z of a single set of cables.
Note on V17: Eric Stromberg: This is the calcuated Z of a single set of cables.
Note on D18: Eric Stromberg: this is the Voltage drop per 1000 feet for the circuit. The calculated value takes into acccount the number of parallel conductors
Note on V18: Eric Stromberg: this is the Voltage drop per 1000 feet for the circuit. The calculated value takes into acccount the number of parallel conductors
Note on D22: Eric Stromberg: This Cell is the distance that is based on the voltage drop formula commonly referred to as the KID formula. It is as follows: Vdrop (1phase) = (2*I*K*D)/(cmil) ….or... Vdrop (3phase) = (sqrt(3)*I*K*D)/(cmil) Where K for copper is 12.9 ...and... Where K for aluminim is 21.2 Although this formula is commonly used, it does not take into account power factor or raceway type. Also, although K is considered a constant, it is not. Whereas this formula is usually more generous when it comes to allowable distances, it is not very good for motor starting when the power factor is around 40%. Using the KID formula for motor starting will result in very large conductor sizes.
Note on V22: Eric Stromberg: This Cell is the distance that is based on the voltage drop formula commonly referred to as the KID formula. It is as follows: Vdrop (1phase) = (2*I*K*D)/(cmil) ….or... Vdrop (3phase) = (sqrt(3)*I*K*D)/(cmil) Where K for copper is 12.9 ...and... Where K for aluminim is 21.2 Although this formula is commonly used, it does not take into account power factor or raceway type. Also, although K is considered a constant, it is not. Whereas this formula is usually more generous when it comes to allowable distances, it is not very good for motor starting when the power factor is around 40%. Using the KID formula for motor starting will result in very large conductor sizes.
Note on D23: Eric Stromberg: This Cell is the distance that is based on the voltage drop formula commonly referred to as the KID formula. It is as follows: Vdrop (1phase) = (2*I*K*D)/(cmil) ….or... Vdrop (3phase) = (sqrt(3)*I*K*D)/(cmil) Where K for copper is 12.9 ...and... Where K for aluminim is 21.2 Although this formula is commonly used, it does not take into account power factor or raceway type. Also, although K is considered a constant, it is not. Whereas this formula is usually more generous when it comes to allowable distances, it is not very good for motor starting when the power factor is around 40%. Using the KID formula for motor starting will result in very large conductor sizes.
Note on V23: Eric Stromberg: This Cell is the distance that is based on the voltage drop formula commonly referred to as the KID formula. It is as follows: Vdrop (1phase) = (2*I*K*D)/(cmil) ….or... Vdrop (3phase) = (sqrt(3)*I*K*D)/(cmil) Where K for copper is 12.9 ...and... Where K for aluminim is 21.2 Although this formula is commonly used, it does not take into account power factor or raceway type. Also, although K is considered a constant, it is not. Whereas this formula is usually more generous when it comes to allowable distances, it is not very good for motor starting when the power factor is around 40%. Using the KID formula for motor starting will result in very large conductor sizes.

## Notes
1 | This spreadsheet was created to compare different options for paralleling conductors. The Green cells are inputs; everything else are outputs. None of the cells are protected, so it may not be a bad idea to keep an original copy of this spreadsheet in case a cell is accidently changed. There are two sets of 8 columns each. The left set shows the minimum conductor size for the selected conditions. All calculations are based in 90deg conductor insulation. If the distance given for the minimum conductor size is not adequate, the user may input a larger conductor size in the right set of 8 columns.
2 | Voltage drop calculations are based on Chapter 9 Table 9. Vd = [R*cos(th) + X*sin(th)]. Table 9 does not include some of the conductor sizes, namely: 700, 800, 900, and anything over 1,000. I didn't know this when I first started writing the spreadsheet so the left 8 columns include these conductor sizes. If the formula picks one of these conductor sizes, most of the voltage drop cells simply go blank.
3 | This spreadsheet does not include any 60 degree ampaciites. 60 degree terminations are largely a thing of the past, as most electrical equipment terminations have been rated at 75 degrees for some time now.
4 | Some of the Ampacities of Table 310.15(B)(16) changed in 2011. These changes are reflected in these tables
5 | The last worksheet "Parallel Conductors" is not used in this spreadsheet for any of the formula; yet. It is used in figuring out what size GEC is needed in the case of parallel conductors.
6 | The spreadsheet has an allowance for continuous loading. If a 100 Amp continuous load is used, the conductors are sized for 125 Amps, but the voltage drop is based on the 100 Amps.

## tables
[15 empty] | 133100 |  | 1200 | [7 empty] | cu | cu | al | al
[15 empty] | 2/0 |  | 3/0 |  |  |  | 250.66 |  |  |  | 85% pf | 85% pf | 85% pf | 85% pf
Table 9 | [8 empty] | 310.15(B)(16) |  | 310.15(B)(16) |  | 240.6 |  |  |  |  | 250.122 |  | Supply |  |  | AWG | CMIL | Air/PVC | Steel | Air/PVC | Steel
conductors | AWG | CMIL | 75degC Amp | 90degC Amp | CCC | Percentage | Ambient - C | Factor | 75degC Amp | AWG - cu | 90degC Amp | AWG - cu | 1 | 15 | CMIL | AWG | Protection | Cu - EGC | Al - EGC | Cond. Size | Cu - GEC | Al - GEC | 14 | 4110 | 2.7 | 2.7
14 | 14 | 4110 | 20 | 25 | 1 | 1 | 10 | 1.15 | 1 | 14 | 1 | 14 | 15 | 15 | 4110 | 14 | 15 | 14 | 12 | 1 | 8 | 6 | 12 | 6530 | 1.7 | 1.7 | 2.8 | 2.8
12 | 12 | 6530 | 25 | 30 | 2 | 1 | 11 | 1.12 | 15 | 14 | 25 | 14 | 15.01 | 20 | 6530 | 12 | 20 | 12 | 10 | 66360 | 8 | 6 | 10 | 10380 | 1.1 | 1.1 | 1.8 | 1.8
10 | 10 | 10380 | 35 | 40 | 3 | 1 | 12 | 1.12 | 15.01 | 12 | 25.01 | 12 | 20 | 20 | 10380 | 10 | 25 | 10 | 8 | 66361 | 6 | 4 | 8 | 16510 | 0.69 | 0.7 | 1.1 | 1.1
8 | 8 | 16510 | 50 | 55 | 4 | 0.8 | 13 | 1.12 | 20 | 12 | 30 | 12 | 20.01 | 25 | 16510 | 8 | 30 | 10 | 8 | 105600 | 6 | 4 | 6 | 26240 | 0.44 | 0.45 | 0.71 | 0.72
6 | 6 | 26240 | 65 | 75 | 5 | 0.8 | 14 | 1.12 | 20.01 | 10 | 30.01 | 10 | 25 | 25 | 26240 | 6 | 35 | 10 | 8 | 105601 | 4 | 2 | 4 | 41740 | 0.29 | 0.3 | 0.46 | 0.46
4 | 4 | 41740 | 85 | 95 | 6 | 0.8 | 15 | 1.12 | 30 | 10 | 40 | 10 | 25.01 | 30 | 41740 | 4 | 40 | 10 | 8 | 167800 | 4 | 2 | 3 | 52620 | 0.23 | 0.24 | 0.37 | 0.37
3 | 3 | 52620 | 100 | 115 | 7 | 0.7 | 16 | 1.08 | 30.01 | 8 | 40.01 | 8 | 30 | 30 | 52620 | 3 | 45 | 10 | 8 | 167801 | 2 | 1/0 | 2 | 66360 | 0.19 | 0.2 | 0.3 | 0.3
2 | 2 | 66360 | 115 | 130 | 8 | 0.7 | 17 | 1.08 | 50 | 8 | 55 | 8 | 30.01 | 35 | 66360 | 2 | 50 | 10 | 8 | 350000 | 2 | 1/0 | 1 | 83690 | 0.16 | 0.16 | 0.24 | 0.25
1 | 1 | 83690 | 130 | 145 | 9 | 0.7 | 18 | 1.08 | 50.01 | 6 | 55.01 | 6 | 35 | 35 | 83690 | 1 | 60 | 10 | 8 | 350001 | 1/0 | 3/0 | 1/0 | 105600 | 0.13 | 0.13 | 0.19 | 0.2
1/0 | 1/0 | 105600 | 150 | 170 | 10 | 0.5 | 19 | 1.08 | 65 | 6 | 75 | 6 | 35.01 | 40 | 105600 | 1/0 | 70 | 8 | 6 | 600000 | 1/0 | 3/0 | 2/0 | 133100 | 0.11 | 0.11 | 0.16 | 0.16
2/0 | 2/0 | 133100 | 175 | 195 | 11 | 0.5 | 20 | 1.08 | 65.01 | 4 | 75.01 | 4 | 40 | 40 | 133100 | 2/0 | 80 | 8 | 6 | 600001 | 2/0 | 4/0 | 3/0 | 167800 | 0.088 | 0.094 | 0.13 | 0.14
3/0 | 3/0 | 167800 | 200 | 225 | 12 | 0.5 | 21 | 1.04 | 85 | 4 | 95 | 4 | 40.01 | 45 | 167800 | 3/0 | 90 | 8 | 6 | 1100000 | 2/0 | 4/0 | 4/0 | 211600 | 0.074 | 0.08 | 0.11 | 0.11
4/0 | 4/0 | 211600 | 230 | 260 | 13 | 0.5 | 22 | 1.04 | 85.01 | 3 | 95.01 | 3 | 45 | 45 | 211600 | 4/0 | 100 | 8 | 6 | 1100001 | 3/0 | 250 | 250 | 250000
250 | 250 | 250000 | 255 | 290 | 14 | 0.5 | 23 | 1.04 | 100 | 3 | 115 | 3 | 45.01 | 50 | 250000 | 250 | 110 | 6 | 4 | ? | 3/0 | 250 | 300 | 300000
300 | 300 | 300000 | 285 | 320 | 15 | 0.5 | 24 | 1.04 | 100.01 | 2 | 115.01 | 2 | 50 | 50 | 300000 | 300 | 125 | 6 | 4 |  |  |  | 350 | 350000
350 | 350 | 350000 | 310 | 350 | 16 | 0.5 | 25 | 1.04 | 115 | 2 | 130 | 2 | 50.01 | 60 | 350000 | 350 | 150 | 6 | 4 |  |  |  | 400 | 400000
400 | 400 | 400000 | 335 | 380 | 17 | 0.5 | 26 | 1 | 115.01 | 1 | 130.01 | 1 | 60 | 60 | 400000 | 400 | 175 | 6 | 4 |  |  |  | 500 | 500000
500 | 500 | 500000 | 380 | 430 | 18 | 0.5 | 27 | 1 | 130 | 1 | 145 | 1 | 60.01 | 70 | 500000 | 500 | 200 | 6 | 4 |  |  |  | 600 | 600000
600 | 600 | 600000 | 420 | 475 | 19 | 0.5 | 28 | 1 | 130.01 | 1/0 | 145.01 | 1/0 | 70 | 70 | 600000 | 600 | 225 | 4 | 2 |  |  |  | 700 | 700000
750 | 700 | 700000 | 460 | 520 | 20 | 0.5 | 29 | 1 | 150 | 1/0 | 170 | 1/0 | 70.01 | 80 | 700000 | 700 | 250 | 4 | 2 |  |  |  | 750 | 750000
1000 | 750 | 750000 | 475 | 535 | 21 | 0.45 | 30 | 1 | 150.01 | 2/0 | 170.01 | 2/0 | 80 | 80 | 750000 | 750 | 300 | 4 | 2 |  |  |  | 800 | 800000
| 800 | 800000 | 490 | 555 | 22 | 0.45 | 31 | 0.96 | 175 | 2/0 | 195 | 2/0 | 80.01 | 90 | 800000 | 800 | 350 | 3 | 1 |  |  |  | 900 | 900000
| 900 | 900000 | 520 | 585 | 23 | 0.45 | 32 | 0.96 | 175.01 | 3/0 | 195.01 | 3/0 | 90 | 90 | 900000 | 900 | 400 | 3 | 1 |  |  |  | 1000 | 100000
| 1000 | 100000 | 545 | 615 | 24 | 0.45 | 33 | 0.96 | 200 | 3/0 | 225 | 3/0 | 90.01 | 100 | 100000 | 1000 | 450 | 2 | 1/0 |  |  |  | 1250 | 1250000
| 1250 | 1250000 | 590 | 665 | 25 | 0.45 | 34 | 0.96 | 200.01 | 4/0 | 225.01 | 4/0 | 100 | 100 | 1250000 | 1250 | 500 | 2 | 1/0 |  |  |  | 1500 | 1500000
| 1500 | 1500000 | 625 | 705 | 26 | 0.45 | 35 | 0.96 | 230 | 4/0 | 260 | 4/0 | 100.01 | 110 | 1500000 | 1500 | 600 | 1 | 2/0 |  |  |  | 1750 | 1750000
| 1750 | 1750000 | 650 | 735 | 27 | 0.45 | 36 | 0.91 | 230.01 | 250 | 260.01 | 250 | 110 | 110 | 1750000 | 1750 | 700 | 1/0 | 3/0 |  |  |  | 2000 | 2000000
| 2000 | 2000000 | 665 | 750 | 28 | 0.45 | 37 | 0.91 | 255 | 250 | 290 | 250 | 110.01 | 125 | 2000000 | 2000 | 800 | 1/0 | 3/0
[5 empty] | 29 | 0.45 | 38 | 0.91 | 255.01 | 300 | 290.01 | 300 | 125 | 125 |  |  | 1000 | 2/0 | 4/0
[5 empty] | 30 | 0.45 | 39 | 0.91 | 285 | 300 | 320 | 300 | 125.01 | 150 |  |  | 1200 | 3/0 | 250
| Y | 1 | PVC/Air | 120 | 31 | 0.4 | 40 | 0.91 | 285.01 | 350 | 320.01 | 350 | 150 | 150 |  |  | 1600 | 4/0 | 350
| N | 3 | Aluminum | 208 | 32 | 0.4 | 41 | 0.87 | 310 | 350 | 350 | 350 | 150.01 | 175 |  |  | 2000 | 250 | 400
|  |  | Steel | 240 | 33 | 0.4 | 42 | 0.87 | 310.01 | 400 | 350.01 | 400 | 175 | 175 |  |  | 2500 | 350 | 600
|  |  |  | 277 | 34 | 0.4 | 43 | 0.87 | 335 | 400 | 380 | 400 | 175.01 | 200 |  |  | 3000 | 400 | 600
|  |  |  | 480 | 35 | 0.4 | 44 | 0.87 | 335.01 | 500 | 380.01 | 500 | 200 | 200 |  |  | 4000 | 500 | 750
[5 empty] | 36 | 0.4 | 45 | 0.87 | 380 | 500 | 430 | 500 | 200.01 | 225 |  |  | 5000 | 700 | 1200
[5 empty] | 37 | 0.4 | 46 | 0.82 | 380.01 | 600 | 430.01 | 600 | 225 | 225 |  |  | 6000 | 800 | 1200
[5 empty] | 38 | 0.4 | 47 | 0.82 | 420 | 600 | 475 | 600 | 225.01 | 250
[5 empty] | 39 | 0.4 | 48 | 0.82 | 420.01 | 700 | 475.01 | 700 | 250 | 250
[5 empty] | 40 | 0.4 | 49 | 0.82 | 460 | 700 | 520 | 700 | 250.01 | 300
[7 empty] | 50 | 0.82 | 460.01 | 750 | 520.01 | 750 | 300 | 300
[7 empty] | 51 | 0.76 | 475 | 750 | 535 | 750 | 300.01 | 350
[7 empty] | 52 | 0.76 | 475.01 | 800 | 535.01 | 800 | 350 | 350
[7 empty] | 53 | 0.76 | 490 | 800 | 555 | 800 | 350.01 | 400
[7 empty] | 54 | 0.76 | 490.01 | 900 | 555.01 | 900 | 400 | 400
[7 empty] | 55 | 0.76 | 520 | 900 | 585 | 900 | 400.01 | 450
[7 empty] | 56 | 0.71 | 520.01 | 1000 | 585.01 | 1000 | 450 | 450
[7 empty] | 57 | 0.71 | 545 | 1000 | 615 | 1000 | 450.01 | 500
[7 empty] | 58 | 0.71 | 545.01 | 1250 | 615.01 | 1250 | 500 | 500
[7 empty] | 59 | 0.71 | 590 | 1250 | 665 | 1250 | 500.01 | 600
[7 empty] | 60 | 0.71 | 590.01 | 1500 | 665.01 | 1500 | 600 | 600
[7 empty] | 61 | 0.65 | 625 | 1500 | 705 | 1500 | 600.01 | 700
[7 empty] | 62 | 0.65 | 625.01 | 1750 | 705.01 | 1750 | 700 | 700
[7 empty] | 63 | 0.65 | 650 | 1750 | 735 | 1750 | 700.01 | 800
[7 empty] | 64 | 0.65 | 650.01 | 2000 | 735.01 | 2000 | 999.99 | 800
[7 empty] | 65 | 0.65 | 665 | 2000 | 750 | 2000 | 1000 | 1000
[7 empty] | 66 | 0.58 | 665.01 | Over | 750.01 | Over | 1200 | 1200
[7 empty] | 67 | 0.58 |  |  |  |  | 1600 | 1600
[7 empty] | 68 | 0.58 |  |  |  |  | 2000 | 2000
[7 empty] | 69 | 0.58 |  |  |  |  | 2500 | 2500
[7 empty] | 70 | 0.58 |  |  |  |  | 3000 | 3000
[7 empty] | 71 | 0.5 |  |  |  |  | 4000 | 4000
[7 empty] | 72 | 0.5 |  |  |  |  | 5000 | 5000
[7 empty] | 73 | 0.5 |  |  |  |  | 6000 | 6000
[7 empty] | 74 | 0.5 | 75degC Amp | AWG - al | 90degC Amp | AWG - al | 6001 | Error
[7 empty] | 75 | 0.5
[7 empty] | 76 | 0.41
[7 empty] | 77 | 0.41 | 1 | 12 | 1 | 12
[7 empty] | 78 | 0.41 | 20 | 12 | 25 | 12
[7 empty] | 79 | 0.41 | 20.01 | 10 | 25.01 | 10
[7 empty] | 80 | 0.41 | 30 | 10 | 35 | 10
[7 empty] | 81 | 0.29 | 30.01 | 8 | 35.01 | 8
[7 empty] | 82 | 0.29 | 40 | 8 | 45 | 8
[7 empty] | 83 | 0.29 | 40.01 | 6 | 45.01 | 6
[7 empty] | 84 | 0.29 | 50 | 6 | 55 | 6
[7 empty] | 85 | 0.29 | 50.01 | 4 | 55.01 | 4
[7 empty] | 85.01 | error | 65 | 4 | 75 | 4
[9 empty] | 65.01 | 3 | 75.01 | 3
[9 empty] | 75 | 3 | 85 | 3
[9 empty] | 75.01 | 2 | 85.01 | 2
[9 empty] | 90 | 2 | 100 | 2
[9 empty] | 90.01 | 1 | 100.01 | 1
[9 empty] | 100 | 1 | 115 | 1
[9 empty] | 100.01 | 1/0 | 115.01 | 1/0
[9 empty] | 120 | 1/0 | 135 | 1/0
[7 empty] | Ambient - F | Factor | 120.01 | 2/0 | 135.01 | 2/0
[7 empty] | 50 | 1.15 | 135 | 2/0 | 150 | 2/0
[7 empty] | 51 | 1.12 | 135.01 | 3/0 | 150.01 | 3/0
[7 empty] | 52 | 1.12 | 155 | 3/0 | 175 | 3/0
[7 empty] | 53 | 1.12 | 155.01 | 4/0 | 175.01 | 4/0
[7 empty] | 54 | 1.12 | 180 | 4/0 | 205 | 4/0
[7 empty] | 55 | 1.12 | 180.01 | 250 | 205.01 | 250
[7 empty] | 56 | 1.12 | 205 | 250 | 230 | 250
[7 empty] | 57 | 1.12 | 205.01 | 300 | 230.01 | 300
[7 empty] | 58 | 1.12 | 230 | 300 | 260 | 300
[7 empty] | 59 | 1.12 | 230.01 | 350 | 260.01 | 350
[7 empty] | 60 | 1.08 | 250 | 350 | 280 | 350
[7 empty] | 61 | 1.08 | 250.01 | 400 | 280.01 | 400
[7 empty] | 62 | 1.08 | 270 | 400 | 305 | 400
[7 empty] | 63 | 1.08 | 270.01 | 500 | 305.01 | 500
[7 empty] | 64 | 1.08 | 310 | 500 | 350 | 500
[7 empty] | 65 | 1.08 | 310.01 | 600 | 350.01 | 600
[7 empty] | 66 | 1.08 | 340 | 600 | 385 | 600
[7 empty] | 67 | 1.08 | 340.01 | 700 | 385.01 | 700
[7 empty] | 68 | 1.08 | 375 | 700 | 425 | 700
[7 empty] | 69 | 1.04 | 375.01 | 750 | 425.01 | 750
[7 empty] | 70 | 1.04 | 385 | 750 | 435 | 750
[7 empty] | 71 | 1.04 | 385.01 | 800 | 435.01 | 800
[7 empty] | 72 | 1.04 | 395 | 800 | 445 | 800
[7 empty] | 73 | 1.04 | 395.01 | 900 | 445.01 | 900
[7 empty] | 74 | 1.04 | 425 | 900 | 480 | 900
[7 empty] | 75 | 1.04 | 425.01 | 1000 | 480.01 | 1000
[7 empty] | 76 | 1.04 | 445 | 1000 | 500 | 1000
[7 empty] | 77 | 1.04 | 445.01 | 1250 | 500.01 | 1250
[7 empty] | 78 | 1 | 485 | 1250 | 545 | 1250
[7 empty] | 79 | 1 | 485.01 | 1500 | 545.01 | 1500
[7 empty] | 80 | 1 | 520 | 1500 | 585 | 1500
[7 empty] | 81 | 1 | 520.01 | 1750 | 585.01 | 1750
[7 empty] | 82 | 1 | 545 | 1750 | 615 | 1750
[7 empty] | 83 | 1 | 545.01 | 2000 | 615.01 | 2000
[7 empty] | 84 | 1 | 560 | 2000 | 630 | 2000
[7 empty] | 85 | 1 | 560.01 | Over | 630.01 | Over
[7 empty] | 86 | 1
[7 empty] | 87 | 0.96
[7 empty] | 88 | 0.96
[7 empty] | 89 | 0.96
[7 empty] | 90 | 0.96
[7 empty] | 91 | 0.96
[7 empty] | 92 | 0.96
[7 empty] | 93 | 0.96
[7 empty] | 94 | 0.96
[7 empty] | 95 | 0.96
[7 empty] | 96 | 0.91
[7 empty] | 97 | 0.91
[7 empty] | 98 | 0.91
[7 empty] | 99 | 0.91
[7 empty] | 100 | 0.91
[7 empty] | 101 | 0.91
[7 empty] | 102 | 0.91
[7 empty] | 103 | 0.91
[7 empty] | 104 | 0.91
[7 empty] | 105 | 0.87
[7 empty] | 106 | 0.87
[7 empty] | 107 | 0.87
[7 empty] | 108 | 0.87
[7 empty] | 109 | 0.87
[7 empty] | 110 | 0.87
[7 empty] | 111 | 0.87
[7 empty] | 112 | 0.87
[7 empty] | 113 | 0.87
[7 empty] | 114 | 0.82
[7 empty] | 115 | 0.82
[7 empty] | 116 | 0.82
[7 empty] | 117 | 0.82
[7 empty] | 118 | 0.82
[7 empty] | 119 | 0.82
[7 empty] | 120 | 0.82
[7 empty] | 121 | 0.82
[7 empty] | 122 | 0.82
[7 empty] | 123 | 0.76
[7 empty] | 124 | 0.76
[7 empty] | 125 | 0.76
[7 empty] | 126 | 0.76
[7 empty] | 127 | 0.76
[7 empty] | 128 | 0.76
[7 empty] | 129 | 0.76
[7 empty] | 130 | 0.76
[7 empty] | 131 | 0.76
[7 empty] | 132 | 0.71
[7 empty] | 133 | 0.71
[7 empty] | 134 | 0.71
[7 empty] | 135 | 0.71
[7 empty] | 136 | 0.71
[7 empty] | 137 | 0.71
[7 empty] | 138 | 0.71
[7 empty] | 139 | 0.71
[7 empty] | 140 | 0.71
[7 empty] | 141 | 0.65
[7 empty] | 142 | 0.65
[7 empty] | 143 | 0.65
[7 empty] | 144 | 0.65
[7 empty] | 145 | 0.65
[7 empty] | 146 | 0.65
[7 empty] | 147 | 0.65
[7 empty] | 148 | 0.65
[7 empty] | 149 | 0.65
[7 empty] | 150 | 0.58
[7 empty] | 151 | 0.58
[7 empty] | 152 | 0.58
[7 empty] | 153 | 0.58
[7 empty] | 154 | 0.58
[7 empty] | 155 | 0.58
[7 empty] | 156 | 0.58
[7 empty] | 157 | 0.58
[7 empty] | 158 | 0.58
[7 empty] | 159 | 0.5
[7 empty] | 160 | 0.5
[7 empty] | 161 | 0.5
[7 empty] | 162 | 0.5
[7 empty] | 163 | 0.5
[7 empty] | 164 | 0.5
[7 empty] | 165 | 0.5
[7 empty] | 166 | 0.5
[7 empty] | 167 | 0.5
[7 empty] | 168 | 0.41
[7 empty] | 169 | 0.41
[7 empty] | 170 | 0.41
[7 empty] | 171 | 0.41
[7 empty] | 172 | 0.41
[7 empty] | 173 | 0.41
[7 empty] | 174 | 0.41
[7 empty] | 175 | 0.41
[7 empty] | 176 | 0.41
[7 empty] | 177 | 0.29
[7 empty] | 178 | 0.29
[7 empty] | 179 | 0.29
[7 empty] | 180 | 0.29
[7 empty] | 181 | 0.29
[7 empty] | 182 | 0.29
[7 empty] | 183 | 0.29
[7 empty] | 184 | 0.29
[7 empty] | 185 | 0.29

## cmil
cu - Term | 2x term | 3x term | 4x term | 5x term | 6x term | 7x term | 8x term | cu - Cond | 2x cond | 3x cond | 4x cond | 5x cond | 6x cond | 7x cond | 8x cond | al - Term | 2x - Term | 3x - Term | 4x - Term | 5x - Term | 6x - Term | 7x - Term | 8x - Term | al - cond | 2x - cond | 3x - cond | 4x - cond | 5x - cond | 6x - cond | 7x - cond | 8x - cond | cu - Cond | 2x cond | 3x cond | 4x cond | 5x cond | 6x cond | 7x cond | 8x cond | Al - Cond | 2x cond | 3x cond | 4x cond | 5x cond | 6x cond | 7x cond | 8x cond
0 | 1500000 | 600000 | 350000 | 250000 | 167800 | 133100 | 105600 | 0 | 1000000 | 500000 | 300000 | 211600 | 167800 | 133100 | 105600 | 0 | 0 | 900000 | 500000 | 350000 | 250000 | 211600 | 167800 | 0 | 1750000 | 700000 | 400000 | 300000 | 211600 | 167800 | 133100 | 750000 | 600000 | 600000 | 350000 | 250000 | 167800 | 133100 | 105600 | 750000 | 250000 | 1000000 | 600000 | 500000 | 350000 | 250000 | 211600
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 105600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 133100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133100 | 0 | 0 | 0 | 0 | 0 | 0 | 133100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 167800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167800 | 0 | 0 | 0 | 0 | 0 | 0 | 167800 | 0 | 0 | 0 | 0 | 0 | 0 | 167800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211600 | 0 | 0 | 0 | 0 | 0 | 0 | 211600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211600
0 | 0 | 0 | 0 | 250000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250000 | 0 | 0 | 0 | 0 | 250000 | 0 | 0 | 0 | 0 | 250000 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 350000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350000 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500000 | 0 | 0 | 0
0 | 0 | 600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600000 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000000 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1750000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 4110
12 | 6530
10 | 10380
8 | 16510
6 | 26240
4 | 41740
3 | 52620
2 | 66360
1 | 83690
1/0 | 105600
2/0 | 133100
3/0 | 167800
4/0 | 211600
250 | 250000
300 | 300000
350 | 350000
400 | 400000
500 | 500000
600 | 600000
700 | 700000
750 | 750000
800 | 800000
900 | 900000
1000 | 100000
1250 | 1250000
1500 | 1500000
1750 | 1750000
2000 | 2000000

## Table 9
|  | X for all conductors |  | R for copper conductors |  |  | R for aluminum conductors
AWG | CMIL | PVC/Air/Al | Steel | PVC/Air | Aluminum | Steel | PVC/Air | Aluminum | Steel
14 | 4110 | 0.058 | 0.073 | 3.1 | 3.1 | 3.1
12 | 6530 | 0.054 | 0.068 | 2 | 2 | 2 | 3.2 | 3.2 | 3.2
10 | 10380 | 0.05 | 0.063 | 1.2 | 1.2 | 1.2 | 2 | 2 | 2
8 | 16510 | 0.052 | 0.065 | 0.78 | 0.78 | 0.78 | 1.3 | 1.3 | 1.3
6 | 26240 | 0.051 | 0.064 | 0.49 | 0.49 | 0.49 | 0.81 | 0.81 | 0.81
4 | 41740 | 0.048 | 0.06 | 0.31 | 0.31 | 0.31 | 0.51 | 0.51 | 0.51
3 | 52620 | 0.047 | 0.059 | 0.25 | 0.25 | 0.25 | 0.4 | 0.41 | 0.4
2 | 66360 | 0.045 | 0.057 | 0.19 | 0.2 | 0.2 | 0.32 | 0.32 | 0.32
1 | 83690 | 0.046 | 0.057 | 0.15 | 0.16 | 0.16 | 0.25 | 0.26 | 0.25
1/0 | 105600 | 0.044 | 0.055 | 0.12 | 0.13 | 0.12 | 0.2 | 0.21 | 0.2
2/0 | 133100 | 0.043 | 0.054 | 0.1 | 0.1 | 0.1 | 0.16 | 0.16 | 0.16
3/0 | 167800 | 0.042 | 0.052 | 0.077 | 0.082 | 0.079 | 0.13 | 0.13 | 0.13
4/0 | 211600 | 0.041 | 0.051 | 0.062 | 0.067 | 0.063 | 0.1 | 0.11 | 0.1
250 | 250000 | 0.041 | 0.052 | 0.052 | 0.057 | 0.054 | 0.085 | 0.09 | 0.086
300 | 300000 | 0.041 | 0.051 | 0.044 | 0.049 | 0.045 | 0.071 | 0.076 | 0.072
350 | 350000 | 0.04 | 0.05 | 0.038 | 0.043 | 0.039 | 0.061 | 0.066 | 0.063
400 | 400000 | 0.04 | 0.049 | 0.033 | 0.038 | 0.035 | 0.054 | 0.059 | 0.055
500 | 500000 | 0.039 | 0.048 | 0.027 | 0.032 | 0.029 | 0.043 | 0.048 | 0.045
600 | 600000 | 0.039 | 0.048 | 0.023 | 0.028 | 0.025 | 0.036 | 0.041 | 0.038
700 | 700000
750 | 750000 | 0.038 | 0.048 | 0.019 | 0.024 | 0.021 | 0.029 | 0.034 | 0.031
800 | 800000
900 | 900000
1000 | 1000000 | 0.037 | 0.046 | 0.015 | 0.019 | 0.018 | 0.023 | 0.027 | 0.025
1250 | 1250000
1500 | 1500000
1750 | 1750000
2000 | 2000000

## Parallel Conductors
AWG | CMIL | 2x | 3x | 4x | 5x | 6x | 7x | 8x
14 | 4110 | 2x: Ungrounded conductors. Sizes below 1/0 are not allowed to be paralleled so they are not included. The smallest parallel set allowed is 2 x 1/0, or 211,200 cmils, which is above 3/0. Therefore, the 'ranges' in table 250.66 don't start until the ungrounded conductors are larger than 3/0. Values below the yellow highlighted region are all above 1100 kcmil, therefore the GEC is 3/0. |  |  |  | 250.66
12 | 6530 | [10 empty] | Conductor
10 | 10380 | [8 empty] | ≤2 | 66360 | 8
8 | 16510 | [8 empty] | 1 | 83690 | 6
6 | 26240 | [8 empty] | 1/0 | 105600 | 6
4 | 41740 | [8 empty] | 2/0 | 133100 | 4 | 12.5%
3 | 52620 | [8 empty] | 3/0 | 167800 | 4
2 | 66360 | [7 empty] | 9x | 2 x 1/0 | 211200 | 2 | 26400 | Over 3/0 through 350
1 | 83690 | [8 empty] | 4/0 | 211600 | 2 | 26450
1/0 | 105600 | 211200 | 316800 | 422400 | 528000 | 633600 | 739200 | 844800 | 950400 | 250 | 250000 | 2 | 31250
2/0 | 133100 | 266200 | 399300 | 532400 | 665500 | 798600 | 931700 | 1064800 | 1197900 | 2 x 2/0 | 266200 | 2 | 33275
3/0 | 167800 | 335600 | 503400 | 671200 | 839000 | 1006800 | 1174600 | 1342400 |  | 300 | 300000 | 2 | 37500
4/0 | 211600 | 423200 | 634800 | 846400 | 1058000 | 1269600 |  |  |  | 3 x 1/0 | 316800 | 2 | 39600
250 | 250000 | 500000 | 750000 | 1000000 | 1250000 | 1500000 |  |  |  | 2 x 3/0 | 335600 | 2 | 41950
300 | 300000 | 600000 | 900000 | 1200000 | 1500000 | 1800000 |  |  |  | 350 | 350000 | 2 | 43750
350 | 350000 | 700000 | 1050000 | 1400000 | 1750000 | 2100000 |  |  |  | 3 x 2/0 | 399300 | 1/0 | 49912.5 | Over 350 through 600
400 | 400000 | 800000 | 1200000 | 1600000 | 2000000 | 2400000 |  |  |  | 400 | 400000 | 1/0 | 50000
500 | 500000 | 1000000 | 1500000 | 2000000 | 2500000 | 3000000 |  |  |  | 4 x 1/0 | 422400 | 1/0 | 52800
600 | 600000 | 1200000 | 1800000 | 2400000 | 3000000 | 3600000 |  |  |  | 2 x 4/0 | 423200 | 1/0 | 52900
700 | 700000 | 1400000 | 2100000 | 2800000 | 3500000 | 4200000 |  |  |  | 500 | 500000 | 1/0 | 62500
750 | 750000 | 1500000 | 2250000 | 3000000 | 3750000 | 4500000 |  |  |  | 2 x 250 | 500000 | 1/0 | 62500
800 | 800000 | 1600000 | 2400000 | 3200000 | 4000000 | 4800000 |  |  |  | 3 x 3/0 | 503400 | 1/0 | 62925
900 | 900000 | 1800000 | 2700000 | 3600000 | 4500000 | 5400000 |  |  |  | 5 x 1/0 | 528000 | 1/0 | 66000
1000 | 1000000 | 2000000 | 3000000 | 4000000 | 5000000 | 6000000 |  |  |  | 4 x 2/0 | 532400 | 1/0 | 66550
1250 | 1250000 | 2500000 | 3750000 | 5000000 | 6250000 | 7500000 |  |  |  | 600 | 600000 | 1/0 | 75000
1500 | 1500000 | 3000000 | 4500000 | 6000000 | 7500000 | 9000000 |  |  |  | 2 x 300 | 600000 | 1/0 | 75000
1750 | 1750000 | 3500000 | 5250000 | 7000000 | 8750000 | 10500000 |  |  |  | 6 x 1/0 | 633600 | 2/0 | 79200 | Over 600 through 1100
2000 | 2000000 | 4000000 | 6000000 | 8000000 | 10000000 | 12000000 |  |  |  | 3 x 4/0 | 634800 | 2/0 | 79350
[10 empty] | 5 x 2/0 | 665500 | 2/0 | 83187.5
[10 empty] | 4 x 3/0 | 671200 | 2/0 | 83900
[10 empty] | 700 | 700000 | 2/0 | 87500
[10 empty] | 2 x 350 | 700000 | 2/0 | 87500
[10 empty] | 7 x 1/0 | 739200 | 2/0 | 92400
[10 empty] | 750 | 750000 | 2/0 | 93750
[10 empty] | 3 x 250 | 750000 | 2/0 | 93750
[10 empty] | 6 x 2/0 | 798600 | 2/0 | 99825
[10 empty] | 800 | 800000 | 2/0 | 100000
[10 empty] | 2 x 400 | 800000 | 2/0 | 100000
[10 empty] | 5 x 3/0 | 839000 | 2/0 | 104875
[10 empty] | 8 x 1/0 | 844800 | 2/0 | 105600
[10 empty] | 4 x 4/0 | 846400 | 2/0 | 105800
[10 empty] | 900 | 900000 | 2/0 | 112500
[10 empty] | 3 x 300 | 900000 | 2/0 | 112500
[10 empty] | 7 x 2/0 | 931700 | 2/0 | 116462.5
[10 empty] | 1000 | 1000000 | 2/0 | 125000
[10 empty] | 2 x 500 | 1000000 | 2/0 | 125000
[10 empty] | 4 x 250 | 1000000 | 2/0 | 125000
[10 empty] | 6 x 3/0 | 1006800 | 2/0 | 125850
[10 empty] | 3 x 350 | 1050000 | 2/0 | 131250
[10 empty] | 5 x 4/0 | 1058000 | 2/0 | 132250
[10 empty] | 8 x 2/0 | 1064800 | 2/0 | 133100
[10 empty] | >1100 |  | 3/0