## Sheet1
NFPA eq.
18
0.06666
20
B - 5.1
1.6856
NFPA eq.
18
0.0084
35
B - 5.2
0.65003
NFPA eq.
0.375
208
2.7
0.1
B- 2-1
38552.8316
B- 2-2
6.9423
B-2-3.2
1.9185
23.0217
NFPA eq.
11
0.0084
B-2-3.3
2.213
26.5555
Note on A22: Refer also to www.usbr.gov/safety/RSHS/sec08.pdf for additional information.
Note on A39: Refer also to www.usbr.gov/safety/RSHS/sec08.pdf for additional information.
Note on C4: Enter value - in inches
Note on C5: Enter time - in seconds
Note on C6: Enter current, greater than or equal to 16 kAmps up to 50 kAmps.
Note on C9: Answer for Incident Energy for an Arc in Open Air
Note on C14: Enter value - in inches
Note on C15: Enter time - in seconds
Note on C16: Enter current, greater than or equal to 16 kAmps up to 50 kAmps.
Note on C19: Answer for Incident Energy for an Arc in a Cubic Box
Note on C23: Enter value - in MVA
Note on C24: Enter value - in volts
Note on C25: Enter value - in % Z
Note on C26: Enter value - in seconds
Note on C29: Answer in amps - for Short Circuit Current
Note on C32: Answer for power in the arc - in MW P=[maximum bolted fault in MVA(bf)] x (0.707) sqrd
Note on C35: Answer for Curable Burn Distance in ft.
Note on C37: Answer for Curable Burn Distance - in inches
Note on C40: Enter value - in MVA rating of the transformer. For transformers with MVA ratings below 0.75 MVA, multiply the transformer MVA rating by 1.25
Note on C41: Enter value - in seconds
Note on C44: Answer for Curable Burn Distance in ft.
Note on C46: Answer for Curable Burn Distance - in inches
EMB = 1038.7 x DB-1.4738 x tA x (.0093 x F2 - .3453 x F + 5.9675)
DB = distance from arc electrodes, inches (for distances 18 in. and greater)
tB = arc duration, seconds (cycles / 60 cycles)
F = bolted fault short circuit current, in kA (for the range of 16 to 50kA)
EMB = maximum 20 in. cubic box incident energy ANSWER
DA = distance from arc electrodes, inches (for distances 18 in. and greater)
tA = arc duration, seconds (cycles / 60 cycles)
F = bolted fault short circuit current, in kA (for the range of 16 to 50kA)
EMA = 5271 x DA-1.9593 x tA x (0.0016 x F2 - 0.0076 x F + 0.8938)
EMA = maximum open arc incident energy ANSWER
cal/cm2
inches
seconds
kA
cal/cm2
inches
seconds
kA
MVA bf = bolted fault MVA at point involved
ISC = {{[MVA Base x 106 ] / [1.732 x V]} x 100 / % Z}
ISC = Short Circuit Current ANSWER
Amps
V = volts
MVA
volts
% Z
seconds
% Z = percent impedance based on transformer MVA
t = time of arc exposure in seconds, (cycles / 60 cycles)
Dc = [ 2.65 x MVA bf x t ] 1/2
Dc = Curable Burn Distance ANSWER
Ft
inches
P = 1.732 x V x Isc 10-6 x 0.7072
MW
P = Maximum Power (in MW) in a 3-phase arc ANSWER
Dc = Curable Burn Distance ANSWER
Equation for Arc in Open Air
Equation for Arc in a Cubic Box
Arc Flash Protection (bolted fault) Boundary
MVA = rating of transformer
V = volts
MVA
% Z
seconds
% Z = percent impedance based on transformer MVA
t = time of arc exposure in seconds, (cycles / 60 cycles)
Dc = [ 53 x MVA x t ] 1/2
Dc = Curable Burn Distance ANSWER
Ft
inches
Dc = Curable Burn Distance ANSWER
Arc Flash Protection (transformer) Boundary
THE INFORMATION IS PROVIDED WITH NO WARRANTY OF ANY KIND, EXPRESS OR IMPLIED. NO USE SHOULD BE MADE OF THE INFORMATION EXCEPT BY FULLY QUALIFIED PROFESSIONALS HAVING FORMED THEIR OWN EVALUATION OF THE INFORMATION FOR THEIR OWN PURPOSES AND APPLICATIONS. INFORMATION BASED ON NFPA 70E. (SS Ver. 13)