## Sheet1
By Mike Holt, Please give credit if you give this away, www.mikeholt.com
Red - Input | Example 1 | Example 2 | Example 3 | Example 4 | Example 5 | Example 6 | Example 7 | Example 8 | Example 9 | Example 10
Line-to-Neutral Volts | 120
Line 1 Calculated Load in Amperes | 75
Line 2 Calculated Load in Amperes | 50
Service Neutral Impedance (ohms) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Ground Resistance (3-point method) | 100 | 75 | 50 | 25 | 10 | 5 | 4 | 3 | 2 | 1
Neutral/Ground Parallel Resistance (ohms) | 0.0999 | 0.099867 | 0.0998 | 0.099602 | 0.09901 | 0.098039 | 0.097561 | 0.096774 | 0.095238 | 0.090909
Line 1 (ohms) | 1.6
Line 2 (ohms) | 2.4
| 1249.2019 | 1249.6026 | 1250.4038 | 1252.8077 | 1260.019 | 1272.0377 | 1278.0469 | 1288.062 | 1308.0916 | 1368.1752
| 16.976 | 16.9814 | 16.9921 | 17.0242 | 17.1204 | 17.2808 | 17.3609 | 17.4946 | 17.7618 | 18.5635
| Example 1 | Example 2 | Example 3 | Example 4 | Example 5 | Example 6 | Example 7 | Example 8 | Example 9 | Example 10
Line 1 - Actual Load in Amperes | 73.5862 | 73.5866 | 73.5875 | 73.59 | 73.5976 | 73.6101 | 73.6162 | 73.6264 | 73.6462 | 73.7024
Line 1 Watts | 8663.8829 | 8663.9832 | 8664.1838 | 8664.7841 | 8666.5723 | 8669.5106 | 8670.9604 | 8673.3486 | 8678.0227 | 8691.2752
Line 1 - Loads Operates at Volts | 117.7379 | 117.7386 | 117.7399 | 117.744 | 117.7562 | 117.7761 | 117.786 | 117.8022 | 117.8339 | 117.9239
Line 2 - Actual Load in Amperes | 50.9425 | 50.9423 | 50.9417 | 50.94 | 50.9349 | 50.9266 | 50.9225 | 50.9158 | 50.9025 | 50.8651
Line 2 Watts | 6228.3424 | 6228.2729 | 6228.134 | 6227.7184 | 6226.4808 | 6224.4476 | 6223.4447 | 6221.7929 | 6218.5614 | 6209.4084
Line 2 - Loads Operates at Volts | 122.2621 | 122.2614 | 122.2601 | 122.256 | 122.2438 | 122.2239 | 122.214 | 122.1978 | 122.1661 | 122.0761
Parallel Neutral/Ground Path in Amperes | 22.6436 | 22.6444 | 22.6458 | 22.65 | 22.6627 | 22.6835 | 22.6937 | 22.7106 | 22.7437 | 22.8374
Neutral Watts | 51.2222 | 51.2084 | 51.1807 | 51.098 | 50.8512 | 50.4451 | 50.2444 | 49.9135 | 49.2643 | 47.4132
Neutral Current in Amperes | 22.621 | 22.6142 | 22.6006 | 22.5598 | 22.4383 | 22.2387 | 22.1402 | 21.978 | 21.6606 | 20.7612
Ground Current in Amperes | 0.022621 | 0.030152 | 0.045201 | 0.090239 | 0.22438 | 0.44477 | 0.55351 | 0.7326 | 1.083 | 2.0761
Touch Voltage from Metal Parts to Earth | 2.2621 | 2.2614 | 2.2601 | 2.256 | 2.2438 | 2.2239 | 2.214 | 2.1978 | 2.1661 | 2.0761
Password to unprotect 1234