Arc Fault Circuit Interrupters and the 2002 National Electrical Code.

By Mike Holt

Wiring and equipment installed in accordance with the National Electrical Code will be protected against arcing faults to a degree by a circuit breaker, fuse, or ground-fault circuit-interrupter. Circuit breakers and fuses are effective in preventing fires caused by conditions under which they are designed to operate. That is, when a short circuit or ground fault occurs the circuit’s overcurrent protection device opens, possibly preventing a fire.

However, the amount of current flow of a high-impedance arc is often too low to cause operation of the protection device, and a fire could occur.

As an aid in reducing the hazard of electrical fires from a parallel arcing fault in the branch circuit wiring, the NEC requires a listed AFCI protection device be installed in branch circuit wiring in dwelling unit bedrooms.

Author’s Comment: See the Back to Basics article on page xx for information on what causes an arc and how a AFCI protection device operates. Also the IEEE paper “The Arc-Fault Circuit Interrupter: An Emerging Product, dated September 1998 is available at, www.mikeholt.com/Newsletters/AFCI.pdf.

The 1999 NEC Rule

210-12. Arc-Fault Circuit-Interrupter Protection

(a) Definition. An arc-fault circuit interrupter is a device intended to provide protection from the effects of arc faults by recognizing characteristics unique to arcing and by functioning to de-energize the circuit when an arc fault is detected.

(b) Dwelling Unit Bedrooms. All branch circuits that supply 125-volt, single-phase, 15- and 20-ampere receptacle outlets installed in dwelling unit bedrooms shall be protected by an arc-fault circuit interrupter(s). This requirement shall become effective January 1, 2002.

The 2002 NEC Rule

210.12 Arc-Fault Circuit-Interrupter Protection.

(A) Definition. An arc-fault circuit interrupter is a device intended to provide protection from the effects of arc faults by recognizing characteristics unique to arcing and by functioning to de-energize the circuit when an arc fault is detected.

(B) Dwelling Unit Bedrooms. All branch circuits that supply 125-volt, single-phase, 15- and 20-ampere receptacle outlets installed in dwelling unit bedrooms shall be protected by an arc-fault circuit interrupter listed to provide protection of the entire branch circuit.

Strike through indicates text that was deleted and underline text indicates text that was added to the 2002 NEC.

Author’s Comment: The 125 V limitation to the requirement means that AFCI protection would not be required for a 240 V baseboard heater or room air conditioner. For more information, visit http://www.mikeholt.com/Newsletters/Newsletters.htm, go to the “Miscellaneous” section and visit my “AFCI” links.

The intent of the change from the 1999 NEC is that arc fault protection be provided for all branch circuits that supply 125-volt, single-phase, 15- and 20-ampere outlets, not just receptacle outlets. In addition, the AFCI must be listed so that it will protect the ‘entire branch circuit’ by de-energize the circuit when an arc fault is detected.

Controversy exists between circuit breaker manufactures and wiring device manufactures that make listed AFCI devices. The circuit breaker manufacture insists that the only acceptable device is the AFCI circuit breaker. Wiring device manufactures take the position that AFCI receptacles listed to protect the entire branch circuit should be suitable and Code compliant.

Both make excellent arguments, but the 2002 NEC is very specific. It requires the AFCI protection device to de-energize the circuit and protect the entire circuit from an arc fault. The only device that can de-energize the circuit when an arc fault is detected is the AFCI circuit breaker. AFCI receptacles of the type listed to detect upstream series arc faults will not de-energize the circuit from parallel type arcing faults that may occur upstream of the device. Therefore they cannot be used to meet the 2002 NEC requirement of 210.12.

Considerations

At the time a dwelling unit is wired, it is hard to tell from looking at the bare walls whether a room will be used as a home office or a bedroom. Also, if you are looking at an efficiency apartment, a room may well be furnished with a foldout couch that is used for sleeping on every night, making it look as much like a bedroom as a living room.

If you are in the practice of using one branch circuit for both lighting and receptacles, the 2002 Change will have no effect. But, the practice of separating the lighting from the receptacle circuits in dwelling unit bedrooms will now require two AFCI circuit breakers, or you’ll place them all on the same circuit do to the cost of AFCI protection.

A new subsection (B) was added to 550.25 to require all branch circuits that supply 15 and 20A, 125V outlets in bedrooms of mobile homes and manufactured homes to be protected by arc-fault circuit interrupter.

Why is AFCI protection only required for dwelling unit branch circuits? The NEC Code panel wanted the industry to gain experience with these devices in bedroom circuits so that in the future their usage might be expanded to other rooms and facilities that could benefit by the added protection to provide. Studies have shown that over 60 percent of fires are from causes in the fixed wiring, switches, receptacle outlets and lighting fixtures that are part of the fixed electrical system of a residence.

# Arc Fault Protection - What it’s all about

“Arcing” is defined as a luminous discharge of electricity across an insulating medium. Electric arcs operate at temperatures between 5,000 and 15,000°F and expel small particles of very hot molten materials. Higher current arcs are more likely to cause a fire because of the higher thermal energy contained in the arc. Greater current will melt more of the conductor metal and therefore expel more hot molten particles.

In electrical circuits unsafe arcing faults can occur in one of two ways, as series arcing faults or as parallel arcing faults. The most dangerous is the parallel. A series arc can occur when the conductor in series with the load is unintentionally broken. Examples might be a frayed conductor in a cord that has pulled apart. A series arc’s current is load limited; the arc’s current cannot be greater than the load current the conductor serves. Typically, series arcs do not develop sufficient thermal energy to create a fire.

Parallel arcing faults occur in either of two ways, as a short circuit or as a ground fault. A short circuit arc might occur if the wire’s insulation is damaged by an excessively or incorrectly driven staple in NM cable, or the insulation of the cord is damaged by a conductive object such as a metal table leg placed on the cord. The result is a decrease in the dielectric strength of insulation separating the conductors allowing a high-impedance low current arcing fault to develop. This arcing fault carbonizes the conductor’s insulation further decreasing the dielectric of the insulation separating the conductors, resulting in an increase in current, an exponential increase in thermal energy heat and the likelihood of a fire.

The current flow in a short-circuit type arc is limited by the system impedance and the impedance of the arcing fault itself. Typically at a receptacle it will be above 75 A, but not likely above 450 A. This short-circuit arc is reported as being more common in older homes where the appliance cords and the building wiring have deteriorated due to the negative effects of ageing.

A ground fault type arc can only occur when a ground path is present. This type of arcing fault can be cleared by either a GFCI or AFCI circuit protective device.

The rms current value for parallel arc faults will be considerably less than that of a solid bolted type fault, therefore a typical 15 A circuit protective device might not clear this fault before a fire is ignited.

AFCI Protection Devices

To help reduce the hazard of electrical fires from a parallel arcing fault in the branch circuit wiring, the 2002 NEC requires a listed AFCI protection device be installed to protect the branch circuit wiring in dwelling unit bedrooms. UL 1699 contains the listing requirement for 15 A and 20 A Arc-Fault Circuit-Interrupter devices, and each type device is intended to protect different aspects of the branch circuit and extension wiring. Current level of detection of parallel arcs is for sensing 8 peaks of arcing at 75 A and above within a 0.5 second window.

However, the only AFCI device that currently meets the 2002 NEC requirements is the Branch/Feeder Type.

## Author’s Comment: Visit http://www.ul.com/regulators/afci/categories.html for more information of the six AFCI types and UL product categories.

Warning: AFCI protection devices are not designed to prevent fires caused by series arcing at loose connections to a receptacle, device or in a splice.

Branch/Feeder Type – This AFCI circuit breaker device is to be installed at the origin of a circuit, such as at a panelboard. It provides parallel arc fault protection for branch circuit wiring, cord sets and power-supply cords. This device is not listed to provide series arc fault protection of extension wiring, but it is listed to protect against series arc faults in NM cable with ground, but not NM cable without ground.

Combination Type  – This device provides both parallel and series arc fault protection for branch circuit wiring, cord sets and power-supply cords downstream of the device. Typically, this device is a receptacle, but it is expected that circuit breakers will be listed for this purpose. This type of device is not tested or listed to provide parallel or series arc fault protection upstream of the device.

Outlet Branch Circuit Type – A device intended to be installed as the first outlet in a branch circuit. It is intended to provide parallel and series protection to downstream branch circuit wiring, cord sets, and power-supply cords. This device also provides series protection to upstream branch circuit wiring.

Outlet Circuit Type – This AFCI device, typically an outlet is installed at a branch circuit outlet and it provides for both parallel and series arcing fault protection of the cord sets and power-supply cords plugged into the outlet. This device is intended to protect extension wiring plugged into the device as well as extensions plugged into downstream receptacles. It does not provide arc fault protection on feed-thru branch circuit conductors, nor is it listed and tested to provide parallel or series arc fault protection upstream of the device.

UL 1699 requires testing of the AFCI devices through a rigorous set of tests for arc detection ability, unwanted operation (to avoid nuisance operation) and operation inhibition. The operation inhibition tests assure that the AFCI will detect an arc even though it may be connected electrically in series or parallel with loads that might attenuate, mask the arc signal.

While all listed electrical devices are subjected to various types of tests intended to confirm safe operation, AFCI devices are subject to an enhanced level of testing. This is due to the daily occurrences of “safe” arcing events that occur in our homes. Arcing is produced from many safely operating electrical appliances, such as universal motors in vacuum cleaners, motor starting relays in refrigerators and portable drills.

While these AFCI devices are relatively new to the NEC, they have undergone several years of testing. Field experience to date indicates they are proving themselves reliable additions in our arsenal of electrical hazard reducing devices.

The following proposals for the 2002 NEC were all rejected:

- The U. S. Consumer Product Safety Commission request that existing bedroom branch circuit be protected by an AFCI when the service equipment is replaced.

- Omit AFCI protection for the lighting outlets, because light may be needed when the AFCI device operates.

- Extend AFCI protection guest room branch circuits of motels and hotels.

- Permit the AFCI receptacle outlet to provide the required protection.

- Omit AFCI protection for the smoke detector circuit conductors.

- Delete the AFCI requirement completely.

Questions about AFCI’s and their installation

Q1. What happens when a bedroom appliance has a locked rotor condition (bedroom window air-conditioner)? Will the AFCI breaker respond?

A1. No and Yes. The waveform signature of locked rotor current is not typical of an arc fault, so the AFCI will not respond. Under locked rotor conditions, either the magnetic function, or in time the thermal trip element of the protection device should open the circuit. Many small air-condition motors will be equipped with a hermetically encased thermal limit device, which will open before the branch circuit protection device. However, if the locked rotor current does not open a protection device, the motor winding will ultimately short-out and the circuit breaker or fuse will open to safely clear the fault.

Q2. Will there be lots of nuisance tripping of these devices?

A2. Honestly there has not been sufficient experience in the field to answer this question, but what might appear to be a nuisance tripping condition might be an actual arc fault. At some point, we will all need to learn how to trace down arcing type faults, perhaps with some type of sensor, perhaps by taking the circuit apart, isolating individual sections. I am not aware of any commercially available meter or instrument that could be used for this purpose.

# Q3. Will a AFCI prevent fires from loose connections at terminals or splicing devices?

# A3. No, this product is not listed to protect against this type of series (glowing) fault, but studies have shown that it does provide some limited protection once the glowing fault becomes a series once the fault becomes.

# Q4. Are there any AFCI/GFCI combination breakers?

A4. Yes

Q5. This product is useless and only serves to put money in the pockets of manufactures.

A5. I don’t think so. The use of AFCI was proposed by the U.S. Consumer Product Safety Commission. The CPSC is an independent Federal Regulatory Agency with the objective of saving lives and keep families safe by reducing the risk of injuries and deaths associated with consumer products. For more information, visit http://cpsc.gov/

Q6. If you have a dedicated line for computer usage, marked Computer only, would this also need to be on AFCI? The reason why we install a separate line for computer equipment is to have a stable, low noise power supply.

A6. Yep, if its in the bedroom.

Q7. Can an AFCI circuit breaker be placed on a multiwire branch circuit?

A7. No, unless the device is a two-pole 120/240 V rated device, as permitted by UL1699. However for existing installations, a AFCI protection device of the Outlet Branch Circuit Type could be used. A shared neutral between two single pole AFCI ‘s will cause the AFCI to trip.

Q8. How is the AFCI tested?

A8. An AFCI will not trip if there is no load applied. If an AFCI is installed and there is no load, then you would not know there is a problem until a load is turned on later. One suggestion is to test the AFCI with a 100 watt lamp.

Q9. I have heard that when a light bulb burns out it draws 150-200 amps for 1/2 cycle and this could cause nuisance tripping of an AFCI.

A9. This is possible.

Q10. If, as in our area, a residence is entirely wired in conduit, wouldn't either type of arc fault result in "popping" the breaker?

A10. Branch circuit wiring in a metal conduit does offer protection against an arc fault. Both parallel arc faults (short circuit and ground fault) and series arc faults (will ultimately create a parallel fault) will be cleared by a circuit breaker or fuse. I am not so sure about nonmetallic conduit. However, to protect the cord plugged into the receptacle, an AFCI outlet type device would be required.

Q11. In old work with a shared neutral up to a point that then is split off, such as to different bedrooms.  If an AFCI device could be wired in at the first available boxes after the split and protect downstream, that should offer the same level of protection as the code is seeking.

A11. Since the NEC does not apply to old work, AFCI protection is not required. If the market desires AFCI protection for old work, then the AFCI branch outlet type might be the best for that application.

- Connect AFCI breaker in a loadcenter.  If a lamp is included in the “load”, it will provide a convenient indication of the load being energized

- Conduct the following tests (to determine intermittent or continuous performance).

_____	Reset, turn handle to the “ON” position, and push the “Test” button. _____	Report the responses in the check boxes below.

_____	Load is energized when breaker is turned on and trips when the test button is pushed.

_____	Load is not energized when breaker is turned on

_____	Breaker trips immediately when turned on

_____	Load is energized when breaker breaker is turned on and remains energized when “Test” button is pushed.

III  Typical Causes of Arcing Faults:

- The circuit in question could have a secondary grounded neutral downstream from the load center

Example: A bare copper ground wire pushed against the neutral screw on a receptacle.

- The circuit in question could have a secondary grounded neutral downstream from the load center

- The neutrals of one or two circuits are all under one wire nut and as soon as there is a load placed on one of the circuits then two breakers will trip since the neutrals are now being shared.

This can be the situation when there are a couple of three switches in the same box.  Neutrals from two individual circuits cannot be combined under one wire nut.

- Improper Installation - staples or other fasteners that pierce or pinch insulation on construction wire and appliance or extension cords that could result in an arcing fault or leakage to ground > 30ma.

- Wire or cords that touch vibrating metal;

- Wire or cord insulation that has cracked from abuse, age, bending stress; corrosion, heat and lightning or power surges

- Damaged appliances with impaired support or insulation for energized electrical parts

- Female portion of receptacle loses tensile strength

By the way, under what practical conditions do you see that an AFCI breaker protects today's wiring methods, such as conductors in EMT, ENT, AC or MC cable?

Can you think of an example where an AFCI circuit breaker would prevent a fire in branch circuit wiring that a GFCI would not?

Do you think a AFCI circuit breaker is listed to protect against fires at loose or poor connections such as often occurs at receptacles, switches, lighting fixtures, fans, etc.? If yes, why do you think that?

Do you think a AFCI circuit breaker is listed to protect against fires resulting at cords or appliances? If yes, why do you think that?

Can you give me some practical examples where a AFCI protection device would make an installation safer for new wiring?

# Q3. Will a AFCI prevent fires from loose connections at terminals or splicing devices?

# A3. No, this product is not listed to protect against this type of series (glowing) fault, but studies have shown that it does provide some limited protection once the glowing fault becomes a series once the fault becomes.

Mike Holt’s Comment: This author questions the true value of this product as it’s currently listed and required by the National Electrcal Code. Some of the issues include the fact that only bedroom circuits are required to be protected, whereas an arc could occur on any circuit in the occupancy. The product is not listed to protect against fires at loose or poor connections such as often occurs at receptacles, switches, lighting fixtures, fans, etc., and this product is not listed to protect against a series arc fault protection of cords and appliances.