March 21, 2002

Minutes of the meeting held March 21, 2002 at the JATC training center at IBEW Local 103 headquarters, 256 Freeport St., Dorchester, Mass

The meeting was called to order at 1:00 PM by the Co-Chair, William Laidler.  Also attending were, Donald Giombetti (Co-Chair), Frederic P. Hartwell (Secretary), James Rogers (Treasurer), Paul Choiniere (Inspector of Wires, Amherst), James Cialdea (IEEE), John Dagnello, John (Rex) Funderburk (MECA), Robert McGann (IAEI), Leo Martin (Education), Gil Moniz (NEMA), James Naughton (Labor), Thomas O’Toole (Labor), J. Kevin Payton (Municipal Inspectors Assn.), Thomas Purpura (Inspector of Wires, Quincy), Robert Petipas (ABC), Steven Scliopou (IEC), Joseph Sheehan (NFPA, nonvoting), and Robert Weston (Inspector of Wires, Barnstable).

The committee took up the question of whether an interim amendment to 210.12 of the Massachusetts Electrical Code should be pursued at this time due to the apparent lack of readiness on the part of the industry in terms of AFCI products that would work on retrofit applications, as anticipated in 210.12(C). Mr. Hartwell distributed a UL White Paper from the group responsible for further standards activity under UL 1699, the applicable product standard. He had anticipated keeping the source of this material confidential, however, several committee members came with their own copies, having downloaded it from the UL website. Mr. Hartwell therefore declared the document to be public information, and discussion proceeded. Numerous Committee members expressed chagrin at the differences between actual product availability and performance as opposed to the information that had been furnished to the Committee at the time of action on Proposals for the 2002 MEC.

Circuit breakers are not required to pass low-level series arcing tests on ungrounded systems, leaving their performance on such systems open to question. Some installations instructions forbid their use on systems without an equipment ground, and although the trend is for manufacturers to be removing such instructions, the breakers are still not being tested to ¶56.2 of UL 1699. Only one major manufacturer has a two-pole circuit breaker suitable for multiwire applications. The Murray installation instructions (circulated at the meeting) do not restrict their product from being installed on such circuits, and yet their product will plainly nuisance trip if so installed. The receptacle form of AFCI will not be on the market until the second half of 2002, at the earliest. Mr. Sheehan pointed out that the CPSC public comment to require AFCI protection on retrofit applications had failed in CMP 2 (Comment 2-68).

The Committee then turned to discussing what form the modification to 210.12 should take. Mr. Sheehan questioned the technical validity of the Massachusetts FPN, since a receptacle type of AFCI could not satisfy the literal wording of the definition in 210.12(A), which is unammended in Massachusetts. He indicated that this had been NFPA’s staff position in responding to informal inquiries on this subject. Mr. Hartwell responded by noting that current technology had effectively created a direct conflict between the terms of the definition and the final panel action in the comment period (Comment 2-78) on 210.12(B), which required AFCI protection that would cover the entire branch circuit, but which had been written in such a way to allow for certain receptacles. He noted that there was a listed receptacle that would do exactly that, and he explained the series rationale behind the panel action and the listing. Mr. Sheehan again expressed astonishment that UL would list such a device given 210.12(A), but Mr. Moniz corroborated Mr. Hartwell’s statement, and Mr. Sheehan, based on the statement from the NEMA representative, said that he would have to accept that statement, and he would need to reevaluate his own position. He also wondered if a TIA would be requested from the manufacturer involved to address the conflict between 210.12(A) and (B). Mr. Hartwell noted that this issue was widespread; he had received an e-mail from Mike Holt that very morning advising that he was about to publish an article that would opine that receptacle-type AFCIs would not meet the NEC, and Mr. Hartwell said that he planned to try and head off that article.

At this point Mr. Martin, supported by Mr. Naughton, indicated that the entire situation was in so much disarray that the Committee should simply withdraw the entire MEC modification to 210.12. Accordingly, he offered the following

MOTION:	To recommend to the BFPR that the MEC amendment to 210.12 be deleted, thereby leaving the section unchanged from the 2002 NEC.

Mr. Hartwell said that would throw the baby out with the bathwater, since the point of the amendment was to create a unified state standard for action during service changes. The chair put the question and it was, by a vote of 9-7-1,

VOTED:	To recommend to the BFPR that the MEC amendment to 210.12 be deleted, thereby leaving the section unchanged from the 2002 NEC.

Informal discussion followed regarding the exact consequences of the vote just taken. Mr. Payton indicated that when inspectors had to deal with this issue hundreds of times in a jurisdiction, it was intolerable to leave no uniform standard on the table. Mr. Weston, having voted on the prevailing side in the previous vote, decided to offer the following

MOTION:	To reconsider the vote previously taken.

After substantial, animated discussion, the Committee decided to recess for ten minutes, and make use of the refreshments graciously provided by the IBEW. After the meeting reconvened, formal discussion resumed. Mr. Rogers then offered the following motion, and two-thirds being agreeable it was

VOTED:	To order the previous question on the motion to reconsider.

Thereupon the chair put the question and it was, by vote of 10-4-3,

VOTED:	To reconsider the action taken on the main motion.

Mr. Hartwell, having circulated wording during the recess, formally offered the following

MOTION:	To amend the main motion by substituting in place thereof the recommendation to the BFPR that an Exception be added to 210.12(C) in the MEC, as follows:

Exception: For panelboard replacements made before January 1, 2005, AFCI protection shall not be required on existing branch circuits.

Mr. Purpura wondered if the exception should be more tightly drawn so as to address what he felt was the real problem. He described an actual loss in his jurisdiction, where the fire department had been called to a bedroom overhead light in an older home, which was smoking. They pulled down the fixture to discover the smoke was coming from the branch circuit and not the outlet. The fire department then opened the ceiling and discovered old armored cable with no bonding strip, which had a low-level failure which resulted in charring of the ceiling joist along an extensive length of the cable, and which required the destruction of the better part of the upstairs ceilings to put out. He noted that the typical 30 mA trip in AFCI devices would have cleared that problem, even though the failure had never reached the point of opening a conventional branch-circuit protective device. He offered the following amendment to the substitution amendment:

MOTION:	To amend the substitute amendment by inserting the word “multiwire” ahead of “branch circuits” and adding the words “and branch circuits without an equipment grounding conductor” to the end of the proposed exception.

Mr. Laidler spoke in opposition, noting that it would require the site electrician (and/or inspector) to examine every bedroom outlet to determine if an equipment grounding conductor were present to the end of the circuit. He noted that often wiring methods without equipment grounding conductors were energized in locations remote from the panelboard by wiring methods that provided an equipment grounding conductor. The Committee members generally expressed the view that an interim change in the Code should be simply stated, and by a vote of 3-12-2 it was

DEFEATED:	To amend the substitute amendment by inserting the word “multiwire” ahead of “branch circuits” and adding the words “and branch circuits without an equipment grounding conductor” to the end of the proposed exception.

The question therefore reverted to the advisability of proceeding with the substitute amendment as opposed to reaffirming action on the original main motion. Some members expressed the view that the NEC clearly did not require the installation of AFCI protection on existing circuits. Mr. Hartwell said that although the NEC was not retroactive, the question of retroactivity was therefore left to the enforcing jurisdictions, which the Committee effectively represented in this matter, and it was therefore the solemn responsibility of the Committee to answer the question. Mr. Choiniere said that in his view Rule 3 of the MEC required the use of AFCIs in retrofit applications, because the instrumentality of circuit protection (the circuit breaker) was being changed in this case, and the electrician was obliged to work to current code. Other members took the opposite view. Mr. Hartwell noted that if anyone needed substantiation for the notion that every local jurisdiction would likely take differing views on this point, the preceding discussion surely proved that point. The chair put the question, and by a vote of 14-2-1, it was

VOTED:	To amend the main motion by substituting in place thereof the recommendation to the BFPR that an Exception be added to 210.12(C) in the MEC, as follows:

Exception: For panelboard replacements made before January 1, 2005, AFCI protection shall not be required on existing branch circuits.

The question therefore became how the Committee would act on the main motion which had been amended by substitution. The chair put the question, and by a vote of 14-2-1 it was

VOTED:	To recommend to the BFPR that an Exception be added to 210.12(C) in the MEC as follows:

Exception: For panelboard replacements made before January 1, 2005, AFCI protection shall not be required on existing branch circuits.

The chair indicated that the statutory notice period for amendments was about to expire for the May BFPR public hearings. He also noted that the BFPR might move on an emergency basis at their next meeting (April 4th, 2002) so relief would come sooner, and which could then be made permanent in May. He also indicated that some BFPR members had expressed interest in exempting smoke detectors from the requirement, and Mr. Hartwell called the Committee’s attention to the letter from Joe Ross making the same recommendation. The sense of the Committee was that the substantiation for exemption for GFCI coverage was not persuasive in terms of applicability to AFCI devices, which functioned differently and which would presumably have a different history in terms of nuisance tripping. Accordingly, no motion was offered to make such an exemption.

Mr. Hartwell returned to a minor point that had emerged during discussion previously, that being whether a minor error may be contained in 210.12(B) of the MEC in that it specifies single-phase circuits. Mr. Purpura had noted that many multiwire branch circuits originate in panelboards fed from two phase legs of a three-phase distribution. He wondered whether these were properly characterized as “single-phase” circuits, and whether we had inadvertently exempted bedrooms fed from such distributions from any AFCI requirement. Mr. Hartwell noted that since there were no 120-volt three-phase distributions applicable to bedrooms in Massachusetts, deleting the term would not invoke the requirement on unintended circuits. He offered a motion, and it was unanimously

VOTED:	To recommend to the BFPR that the words “single-phase” be deleted from 210.12(B) of the MEC, simultaneously with the action on the exception to 210.12(C).

The chair now turned to another request for interim action in the MEC, that being to exempt the feeders to and/or the distribution equipment for isolated power systems in hospital operating rooms from the enhanced fire separation requirements of MEC 700.9(D). Mr. Sheehan questioned whether this amendment was intended to apply to the critical branch of a hospital, or only the life safety branch. He noted that the MEC position had attracted the attention of the American Hospital Association, which observed that no other jurisdiction applied such restrictive requirements in this area. Mr. Hartwell traced the history of MEC 700.9(D)(1) Ex. to demonstrate the clear intention to include the critical branch, although he said he was inclined to agree with the technical substantiation to exempt this particular feeder and associated equipment. Mr. Laidler noted that he had repeatedly requested that the submitter present his views in the form of a MEC Proposal, since this had first reached the BFPR early in 2000, and that the submitter had failed to submit in a timely way. Mr. Rogers said that interim amendments should only be entertained when there was a true emergency, and this did not rise to that level. The Committee unanimously

VOTED:	To decline to recommend to the BFPR any interim amendment on this subject.

The Committee adjourned at 4:10 PM.