## Sheet1
|  |  | Run Amps | Start Amps
Mike Holt Generator Sizer - Propane (LP) |  |  | 70.8 | 141.7
Running Current | 48 |  | Running current is a condition with all loads expected or desired to be on at any given time.
Largest A/C Compressor Nameplate RLA | 20
Largest A/C Compressor Fan Nameplate RLA/FLA | 3
Largest A/C Compressor Nameplate LRA | 100
Second Largest A/C Compressor Nameplate RLA | 15
Second Largest A/C Compressor Fan Nameplate RLA/FLA | 2
Second Largest A/C Compressor Nameplate LRA | 80
No Load Shed and No Soft Start | Amperes | kW
Running Current | 48 | 11.52 | Running current is a condition with all loads expected or desired to be on at any given time.
Surge Current - Running Current with Largest A/C Starting (LRA) | 125
Load Shed Largest A/C | Amperes | kW
Running Current, less largest A/C current | 25 | 6 | In this case, it's running current less the largest a/c load
Surge Current - Running Current with 2nd Largest A/C Starting (LRA) | 88 |  | In this case, it's running current less the largest and second largest a/c load, plus the second largest a/c starting current
Soft Start Largest A/C | Amperes | kW
Running Current | 48 | 11.52 | Running current is a condition with all loads expected or desired to be on at any given time.
Surge Current - Running Current with Largest A/C Starting (LRA) | 65 |  | In this case, it's running current less the largest a/c current, plus the largest a/c starting current
|  |  | Run Amps | Start Amps
Mike Holt Generator Sizer - Natural Gas (NG) |  |  | 70.8 | 141.6667
Running Current | 48 |  | Running current is a condition with all loads expected or desired to be on at any given time.
Largest A/C Compressor Nameplate RLA | 20
Largest A/C Compressor Fan Nameplate RLA/FLA | 3
Largest A/C Compressor Nameplate LRA | 100
Second Largest A/C Compressor Nameplate RLA | 15
Second Largest A/C Compressor Fan Nameplate RLA/FLA | 2
Second Largest A/C Compressor Nameplate LRA | 80
No Load Shed and No Soft Start | Amperes | kW
Running Current - Largest & Second Largest A/C's running | 48 | 11.52 | Running current is a condition with all loads expected or desired to be on at any given time.
Surge Current - Running Current with Largest A/C Starting (LRA) | 125
Load Shed Largest A/C | Amperes | kW
Running Current - Largest A/C off and all other A/C's running | 25 | 6 | In this case, it's running current less the largest a/c load
Surge Current - Running Current with 2nd Largest A/C Starting (LRA) | 88 |  | In this case, it's running current less the largest and second largest a/c load, plus the second largest a/c starting current
Soft Start Largest A/C | Amperes | kW
Running Current - Largest & Second Largest A/C's running | 48 | 11.52 | Running current is a condition with all loads expected or desired to be on at any given time.
Surge Current - Running Current with Largest A/C Starting (LRA) | 65 |  | In this case, it's running current less the largest a/c current, plus the largest a/c starting current
Mike Holt Generator Sizer - Portable
Running Current with NO a/c's running or Starting | 48 | 11.52